## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8089604 | B106 | Westville Autohouse | 26 Jul 2017 | Centre fridge temp is too high | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Reset pressure switch. Adjusted timer and thermostat. Returned to site and replace the thermostat with new. , |  | 2 | 450 | 900 | 1203 | Thermostat , | 116 | 986 | 3089 | 432.46 | 3521.46
8087694 | B106 | BP John Ross | 31 Jul 2017 | Walk in chiller is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Found gas leak. Cut off damaged section of pipe and elbow to dispose. Fitted new pipe and fittings. Topped up with gas. Pressure tested and found no leaks. , |  | 3 | 563 | 1689 | 2678 | R22 Gas, Copper pipe and fittings, | 30 | 255 | 4622 | 647.08 | 5269.08
8090149 | B106 | BP Raisethorpe | 02 Aug 2017 | Island chiller not working - temp too high | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Repaired gas leak on the expansion valve and re-gassed the unit. Replaced faulty timer with new. , |  | 2 | 450 | 900 | 2500 | R404A gas , Defrost timer , | 170 | 1445 | 4845 | 678.3 | 5523.3
8089668 | B106 | BP Cascades Service Station | 02 Aug 2017 | Cable on the roof is leaking | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Create a safe barricaded work area. Remove and replace the armflex pipe insulation which is connected to the deep freezer. Clean and make work area safe., |  | 2 | 450 | 900 | 1357.2 | Armaflex 5/8 x 3/4, Armaflex Tape, Armaflex 4/8 x 3/4, | 176 | 1496 | 3753.2 | 525.45 | 4278.65
8090330 | B106 | BP Bluff | 02 Aug 2017 | WBC deep freezer is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Checked all electrical connections. Tested and adjusted defrost run timer., |  | 1 | 450 | 450 | 0 | , | 60 | 510 | 960 | 134.4 | 1094.4
8089993 | B106 | BP Ridge Oasis | 02 Aug 2017 | Under counter fridge is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Repaired burnt wiring and topped up unit with gas. , |  | 2 | 450 | 900 | 950 | R134A Gas, | 98 | 833 | 2683 | 375.62 | 3058.62
[8 empty] | 12 |  | 5739 | 8688.2 |  | 650 | 5525 | 19952.2 | 2793.31 | 22745.51