## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8090053 | B109 | BP Kwa Mashu Service Station | 08 Aug 2017 | WBC freezer is not working .. .. | Reactive Maintenance | Isolate the power to the freezer unit and place a lock out. Supply and install a new Danfoss electronic temperature control unit with a smart defrost and a Probe sensor. Prepare and rewire the electronic control unit and Probe sensor. Recommission the freezer unit and conduct a test to ensure that the freezer is correctly functioning. , |  | 2 | 450 | 900 | 3806.48 | Danfoss Electronic Temperature Control Unit, Sensor Cable, Probe Sensor, | 19 | 161.5 | 4867.98 | 681.52 | 5549.5
8090650 | B109 | BP Bluff | 08 Aug 2017 | Freezer room has iced up again | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Found the unit was out of gas due to a gas leak. Repaired gas leak and charged unit with gas., |  | 1 | 450 | 450 | 2100 | R404A gas , | 70 | 595 | 3145 | 440.3 | 3585.3
8090836 | B109 | BP Prospecton Road Service Sta | 08 Aug 2017 | Dairy chiller no 2 is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Removed leaking pipe and fitted new. Tested and found no leaks. Topped up unit with gas. , |  | 1 | 450 | 450 | 879 | R22 Gas, Copper pipe and fittings , | 68 | 578 | 1907 | 266.98 | 2173.98
8090798 | B109 | BP Arena Park | 08 Aug 2017 | No cold air in store, stock is melting | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Defrosted coil and adjusted controller., |  | 2 | 563 | 1126 | 0 | , | 60 | 510 | 1636 | 229.04 | 1865.04
8090635 | B109 | Moore Rd Service Station | 08 Aug 2017 | Dairy chiller cooling but product temp is too warm | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Adjusted gas pressure, temp settings and defrost cycles. Topped up unit with gas., |  | 2 | 450 | 900 | 950 | R404A gas , | 52 | 442 | 2292 | 320.88 | 2612.88
8090530 | B109 | BP Kwa Mashu Service Station | 08 Aug 2017 | Dairy chiller is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Topped up gas, adjusted controller and defrost timer., |  | 1 | 450 | 450 | 1600 | R404A gas , | 0 | 0 | 2050 | 287 | 2337
8091297 | B109 | BP Northdene | 08 Aug 2017 | Freezer room is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Found water in the electrics. Isolated and dried out water. Reset the control breaker. Tested and found no faults. , |  | 2 | 750 | 1500 | 0 | , | 60 | 510 | 2010 | 281.4 | 2291.4
8090961 | B109 | BP Kwa Mashu Service Station | 08 Aug 2017 | Freezer room temp very high | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Found solenoid wiring burnt. Isolated using lock out tag out method. Reset the controller and adjusted the temperature. Repaired burnt wiring. Tested and found no further faults. , |  | 1 | 450 | 450 | 159 | Wiring, tape and gloves , | 32 | 272 | 881 | 123.34 | 1004.34
[8 empty] | 12 |  | 6226 | 9494.48 |  | 361 | 3068.5 | 18788.98 | 2630.46 | 21419.44