## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8095170 | B121 | BP Kwa Mashu Service Station | 06 Sep 2017 | Freezer water pipe leaks. Damaged | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Conducted assessment and found the 50mm elbow damaged. Returned to site and broke concrete wall to removed the damaged pipe. Replaced with new pipe and fittings. Patched up wall with concrete mix and painted to a neat finish. , |  | 3 | 450 | 1350 | 639 | 50mm elbow and pipe , Concrete mix and paint , | 34 | 289 | 2278 | 318.92 | 2596.92
8094747 | B121 | BP Sibaya | 08 Sep 2017 | Air con not cooling -error code 10 | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Reset the unit and cleaned condenser coils. The unit is badly corroded causing it to trip on HP. The unit must be replaced to eliminate the problem. , |  | 1 | 450 | 450 | 175 | Coil cleaner , | 60 | 510 | 1135 | 158.9 | 1293.9
8094798 | B121 | Reservoir Hills Service Statio | 08 Sep 2017 | Shop air con is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found v-belt snapped. Replaced with new and tested all functions. , |  | 2 | 450 | 900 | 450 | Fan v-belt , | 32 | 272 | 1622 | 227.08 | 1849.08
8095003 | B121 | BP Church Street | 08 Sep 2017 | Office air con is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found the universal board not responding to the remote. Reset the unit on the breaker and switched on temporarily on the PC board. We suggest replacing the unit due to it being old and will be problematic. , |  | 1 | 450 | 450 | 0 | , | 175 | 1487.5 | 1937.5 | 271.25 | 2208.75
8093698 | B121 | Westville Autohouse | 08 Sep 2017 | Centre store chiller is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cordon off work area, assessed and found the defrost timer was faulty. Replaced with new. Tested and found unit was working efficiently. , |  | 1 | 488 | 488 | 996 | Legrand Defrost Timer , | 58 | 493 | 1977 | 276.78 | 2253.78
[8 empty] | 8 |  | 3638 | 2260 |  | 359 | 3051.5 | 8949.5 | 1252.93 | 10202.43