## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8094226 | B122 | Moore Rd Service Station | 14 Sep 2017 | Walk in freezer does not reach correct temp | Reactive Maintenance | Arrived on site.Inspected walk in freezer and found out unit is still under guarantee., |  | 0 | 400 | 0 | 800 | Call out charges as agreed., | 0 | 0 | 800 | 112 | 912
8095297 | B122 | BP Church Street | 14 Sep 2017 | Cashier air con not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cordon off work area. Inspected and found the indoor unit frosted up, short of gas and blower wheel blocked. Opened unit cleaned blower wheel, repaired gas leak and topped up gas.Tested unit and found unit cooling well., |  | 2 | 450 | 900 | 800 | R22 Gas, Cleaning agent , | 176 | 1496 | 3196 | 447.44 | 3643.44
8095359 | B122 | BP Prospecton Road Service Sta | 14 Sep 2017 | Shop air con leaking water | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents.Cordoned off work area.Inspected and discovered drain pipe blocked at outlet p-train.Opened unit and flushed out drainage., |  | 1 | 450 | 450 | 0 | , | 45 | 366.75 | 816.75 | 114.35 | 931.1
8095352 | B122 | BP Arena Park | 14 Sep 2017 | Shop air con is not working again | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents.cordoned off work area.Topped up gas on both compressors and insulated outdoor unit., |  | 3 | 563 | 1689 | 1400 | R22 Gas, | 40 | 326 | 3415 | 478.1 | 3893.1
8095205 | B122 | BP Kwa Mashu Service Station | 14 Sep 2017 | Office air con not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found aircon switched off at breaker. Reset and advised dealer how to use., |  | 1 | 450 | 450 | 0 | , | 35 | 285.25 | 735.25 | 102.94 | 838.19
8095577 | B122 | BP Church Street | 14 Sep 2017 | Dairy chiller not correct temp | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents.Cordoned off work area. Assessed and found compressors overheated due to both condenser fans getting seized. Replaced both condenser fans with new. Tested and found no faults. , |  | 3 | 563 | 1689 | 2050 | Conderser fan motor, R22 Gas, | 180 | 1467 | 5206 | 728.84 | 5934.84
[8 empty] | 10 |  | 5178 | 5050 |  | 476 | 3941 | 14169 | 1983.67 | 16152.67