## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8096085 | B127 | BP Dube Village Mall | 14 Sep 2017 | shop roof is leaking , ceiling damaged | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cordon off work area to make safe. Washed filters on the unit and flushed drainage. , |  | 1 | 450 | 450 | 0 | , | 38 | 323 | 773 | 108.22 | 881.22
8096590 | B127 | Drive In Motors | 21 Sep 2017 | Cold room is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found gas pressure was low. Charged the unit with R404a gas. , |  | 1 | 450 | 450 | 650 | R404A Gas, | 82 | 697 | 1797 | 251.58 | 2048.58
8093485 | B127 | Drive In Motors | 21 Sep 2017 | Door glides are faulty to freezer door | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found the door glides were faulty. Replaced and tested operation. , |  | 1 | 450 | 450 | 1650 | Door guide, | 0 | 0 | 2100 | 294 | 2394
8096571 | B127 | BP Dube Village Mall | 21 Sep 2017 | Shop air con is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Replaced faulty control panel. , |  | 1 | 563 | 563 | 2411 | Control Panel , | 38 | 323 | 3297 | 461.58 | 3758.58
8096475 | B127 | BP Clare Road | 21 Sep 2017 | WBC chest freezer is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cordon off work area and repaired the electrics on the wild bean. , |  | 2 | 450 | 900 | 0 | , | 32 | 272 | 1172 | 164.08 | 1336.08
8096632 | B127 | Moore Rd Service Station | 21 Sep 2017 | Dairy upright chiller is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Found no air flow due to the unit being iced up. Switch the unit off to defrost and adjusted the controller. , |  | 1 | 450 | 450 | 0 | , | 52 | 442 | 892 | 124.88 | 1016.88
8096729 | B127 | BP Raisethorpe | 21 Sep 2017 | Cold drinks chiller is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Attended to site and assessed. Found the circuit breakers were faulty. Replaced with new. Left site with the chiller working effectively. Was called back to site by the dealer. Repaired and rewired burnt wiring on the cold room roof., |  | 2 | 563 | 1126 | 972 | Circuit breaker 3 Phase , | 340 | 2890 | 4988 | 698.32 | 5686.32
8096134 | B127 | BP Clare Road | 21 Sep 2017 | Cold room is leaking water | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found the cold room floor was water logged. We recommend waterproofing the floor. , |  | 1 | 450 | 450 | 0 | , | 32 | 272 | 722 | 101.08 | 823.08
8096222 | B127 | BP Raisethorpe | 21 Sep 2017 | Dairy chiller is sitting at high temp | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Unit tripped on HP pressure. Cleaned out condenser and reset the switch. Adjusted temperature. , |  | 2 | 450 | 900 | 0 | , | 170 | 1445 | 2345 | 328.3 | 2673.3
8096208 | B127 | BP Waterloo | 21 Sep 2017 | Freezer is not freezing . . . . . | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found condenser fan motor burnt. Bypass the fan motor and ordered new single phase motor. Returned to site and replaced the condenser fan motor with new., |  | 3 | 563 | 1689 | 1990.4 | Condenser fan motor , | 68 | 578 | 4257.4 | 596.04 | 4853.44
8096412 | B127 | La Lucia Ridge Oasis | 21 Sep 2017 | Dairy chiller temp too high | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cleaned out condenser coils and replaced 25 watt fan motor with new. , |  | 2 | 450 | 900 | 774 | Fan motor , Coil cleaner , | 30 | 255 | 1929 | 270.06 | 2199.06
8087339 | B127 | BP Kwa Mashu Service Station | 21 Sep 2017 | Air con is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found the power button on the remote was faulty. Returned to site and replaced with a new remote. , |  | 1 | 563 | 563 | 0 | Remote control , | 0 | 0 | 563 | 78.82 | 641.82
[8 empty] | 18 |  | 8891 | 8447.4 |  | 882 | 7497 | 24835.4 | 3476.96 | 28312.36