## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8096982 | B132 | Chess Service Station | 02 Oct 2017 | Upright dairy chiller is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found air is not circulating efficiently. Re-positioned mounting plate for evaporator fan., |  | 1 | 450 | 450 | 0 | , | 52 | 442 | 892 | 124.88 | 1016.88
8098659 | B132 | BP Kwa Mashu Service Station | 05 Oct 2017 | Ice freezer temp too low | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Fitted new schrader valve and topped up unit with R404A gas. , |  | 2 | 450 | 900 | 1839 | Schrader valve , R404A Gas, | 34 | 289 | 3028 | 423.92 | 3451.92
8098145 | B132 | BP Northdene | 05 Oct 2017 | Main freezer is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Replaced burnt contactor with new and rewired. Tested and found all in order. , |  | 1 | 450 | 450 | 750 | Contactor , | 60 | 510 | 1710 | 239.4 | 1949.4
8098120 | B132 | BP Bluff | 05 Oct 2017 | No cold air from air con | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cordon off work area to make safe. Assessed and found the unit had a gas leak. Repaired gas leak and charged up the unit with gas. Pressure tested and found no leaks. , |  | 2 | 563 | 1126 | 1360 | R22 Gas, | 60 | 510 | 2996 | 419.44 | 3415.44
[8 empty] | 6 |  | 2926 | 3949 |  | 206 | 1751 | 8626 | 1207.64 | 9833.64