## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8096739 | B134 | BP Umbilo | 05 Oct 2017 | Shop air con is leaking water | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found the PC board was faulty. Ordered parts. Returned to site and replaced with new. , |  | 5 | 450 | 2250 | 4189 | Display panel PC board , | 124 | 1054 | 7493 | 1049.02 | 8542.02
8098658 | B134 | BP Kwa Mashu Service Station | 05 Oct 2017 | Dairy freezer not cooling .. .. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found the coil iced up. Switched on defrost to clear ice build up. Reset thermostat and adjusted the defrost settings. , |  | 2 | 450 | 900 | 0 | , | 34 | 289 | 1189 | 166.46 | 1355.46
8098122 | B134 | BP Bluff | 05 Oct 2017 | Chiller is leaking water ... ... | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cordon off work area. Unblocked the drain and replaced the faulty fan motor with new. , |  | 2 | 563 | 1126 | 782 | Fan motor , | 60 | 510 | 2418 | 338.52 | 2756.52
8097433 | B134 | BP John Ross | 12 Oct 2017 | Beverage fridge lights are not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Replaced faulty ballasts with new. , |  | 1 | 450 | 450 | 710 | Ballast, | 30 | 255 | 1415 | 198.1 | 1613.1
8096470 | B134 | BP John Ross | 12 Oct 2017 | Upright chiller is not working | Reactive Maintenance | Isolate the power to the dairy chiller. Supply and install a new compressor and dryer. Prepare and re-gas the unit. Recommission and conduct a test to ensure that the dairy chiller is correctly functioning., |  | 6 | 450 | 2700 | 16997.5 | Dryer, R22 Gas, Compressor, | 304 | 2584 | 22281.5 | 3119.41 | 25400.91
8099729 | B134 | BP Sibaya | 13 Oct 2017 | Shop air con running error code E10 | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Unit reset by dealer. No fault or error code on unit. Call out charges apply, |  | 0 | 325 | 0 | 800 | Call out charge , | 0 | 0 | 800 | 112 | 912
8099526 | B134 | BP Sibaya | 13 Oct 2017 | Chiller unit not working , tripping on DB | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and insulated the power box. Returned to site and found the solenoid valve exposed. Replaced solenoid head and silicone around the head to seal. , |  | 3 | 450 | 1350 | 282 | Silicone and solenoid head , | 65 | 552.5 | 2184.5 | 305.83 | 2490.33
8099442 | B134 | Drive In Motors | 13 Oct 2017 | Freezer room temp too high | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Removed excess ice from the blower coil and topped up the unit with gas. , |  | 2 | 450 | 900 | 1650 | R404A Gas, | 70 | 595 | 3145 | 440.3 | 3585.3
8099266 | B134 | Araf Fuel Centre | 13 Oct 2017 | Chiller is leaking water .. .. .., | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Flushed out drain pipe and cleaned. , |  | 2 | 750 | 1500 | 0 | , | 60 | 510 | 2010 | 281.4 | 2291.4
8097716 | B134 | BP Sibaya | 13 Oct 2017 | Freezer in WBC ice is building up | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Met with the engineer on site to assess. Cleared out ice build up. , |  | 2 | 450 | 900 | 0 | , | 60 | 510 | 1410 | 197.4 | 1607.4
8096881 | B134 | Daniels Auto Centre | 13 Oct 2017 | Upright chiller is not working | Reactive Maintenance | Isolate the power to the dairy chiller. Supply and install 2 new Copeland (existing) compressor and dryers. Prepare and re-gas the unit. Recommission and conduct a test to ensure that the dairy chiller is correctly functioning. , |  | 10 | 450 | 4500 | 16472.8 | Copeland Compressor, R22 Gas, Dryer, | 172 | 1462 | 22434.8 | 3140.87 | 25575.67
[8 empty] | 35 |  | 16576 | 41883.3 |  | 979 | 8321.5 | 66780.8 | 9349.31 | 76130.11