## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8100593 | B135 | New Germany Service Centre | 18 Oct 2017 | The lights on the door for the cool drink fridge is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Replaced burnt fluorescent globe with new. , |  | 1 | 450 | 450 | 212 | 6ft Fluorescent Globe , | 60 | 510 | 1172 | 164.08 | 1336.08
8100284 | B135 | BP Sibaya | 23 Oct 2017 | Dairy chiller temp too high | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Adjusted temp on controller., |  | 1 | 450 | 450 | 0 | , | 70 | 595 | 1045 | 146.3 | 1191.3
8099546 | B135 | BP Prospecton Road Service Sta | 23 Oct 2017 | Air con is not cooling ... .... | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Defrosted and requested dealer to switch on next day., |  | 1 | 450 | 450 | 0 | , | 65 | 552.5 | 1002.5 | 140.35 | 1142.85
8099538 | B135 | BP Prospecton Road Service Sta | 23 Oct 2017 | Chiller is leaking water .. ... ... | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Found water overflowing onto the floor. Returned to site and re-route drain to external drain., |  | 2 | 450 | 900 | 0 | , | 72 | 612 | 1512 | 211.68 | 1723.68
8099599 | B135 | Reservoir Hills Service Statio | 23 Oct 2017 | Freezer room is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Adjusted blower coil and defrost timer., |  | 2 | 450 | 900 | 0 | , | 34 | 289 | 1189 | 166.46 | 1355.46
8099540 | B135 | BP Prospecton Road Service Sta | 23 Oct 2017 | Upright freezer in WBC is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Adjusted defrost timer of set point., |  | 1 | 450 | 450 | 0 | , | 0 | 0 | 450 | 63 | 513
8099331 | B135 | BP Bluff | 23 Oct 2017 | Chiller is not reaching temp | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Adjusted defrost setting and thermostat setting. Topped up gas charge., |  | 1 | 450 | 450 | 650 | R22 Gas, | 60 | 510 | 1610 | 225.4 | 1835.4
8100248 | B135 | New Germany Service Centre | 23 Oct 2017 | Chiller temp too high . . . | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Washed out filter and adjusted temperature. , |  | 1 | 450 | 450 | 0 | , | 60 | 510 | 960 | 134.4 | 1094.4
8099667 | B135 | BP Bluff | 23 Oct 2017 | Drinks chiller is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Found PC board faulty. Ordered new. Returned and replaced PC board with new. , |  | 3 | 450 | 1350 | 3982 | PC Board, | 120 | 1020 | 6352 | 889.28 | 7241.28
8100098 | B135 | BP Cascades Service Station | 23 Oct 2017 | Chiller is not working again | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Repaired gas leak. Replaced condenser fan motor and topped up gas., |  | 2 | 563 | 1126 | 1879 | Fan Motor , R22 Gas, | 176 | 1496 | 4501 | 630.14 | 5131.14
8096837 | B135 | BP West Street | 24 Oct 2017 | AIRCON PIPE IS LEAKING.NOW THE PLACE IS FLOODED. CAUSING PROBLEMS WITH THE BUILDING MANAGEMENT | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Found leak and repaired leaking distributor. Re-gassed the unit and tested. Found no leaks. , |  | 3 | 563 | 1689 | 650 | R22 Gas, | 52 | 442 | 2781 | 389.34 | 3170.34
8101399 | B135 | BP Escombe | 25 Oct 2017 | Beverage chiller lights are not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and commenced to supplier to purchase new globes. Replaced 2x 6 feet globes with new. , |  | 2 | 450 | 900 | 424 | 6ft Fluorescent Globe , | 0 | 0 | 1324 | 185.36 | 1509.36
[8 empty] | 20 |  | 9565 | 7797 |  | 769 | 6536.5 | 23898.5 | 3345.79 | 27244.29