## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8098763 | B143 | BP Dube Village Mall | 05 Oct 2017 | Air con is leaking water | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Stripped air con, cleaned out base and flushed out drain line. , |  | 2 | 450 | 900 | 0 | , | 34 | 289 | 1189 | 166.46 | 1355.46
8102665 | B143 | BP John Ross | 30 Nov 2017 | Beverage chiller is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Removed from defrost cycle and tested for normal operation., |  | 1 | 483.75 | 483.75 | 0 | , | 40 | 366 | 849.75 | 118.97 | 968.72
8104188 | B143 | BP John Ross | 30 Nov 2017 | Freezer room is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Adjusted defrost time and checked operation., |  | 1 | 483.75 | 483.75 | 0 | , | 40 | 366 | 849.75 | 118.97 | 968.72
8103651 | B143 | BP John Ross | 30 Nov 2017 | Ice freezer is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Defrosted evaporator coil, replaced pressure switch and tested for normal operation., |  | 4 | 483.75 | 1935 | 1270 | Dual pressure switch , | 52 | 475.8 | 3680.8 | 515.31 | 4196.11
8103921 | B143 | Chess Service Station | 30 Nov 2017 | Lights not working in walk in chiller | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Replaced faulty ballast and two globes., |  | 1 | 483.75 | 483.75 | 603 | Ballast 58W, Light bulbs , | 60 | 549 | 1635.75 | 229.01 | 1864.76
8103859 | B143 | BP Raisethorpe | 30 Nov 2017 | Walk in chiller is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Repaired burnt wiring, replaced ballast and 2 x globe holders., |  | 1 | 483.75 | 483.75 | 564.98 | Ballast 58W, Light bulb holders , | 170 | 1555.5 | 2604.23 | 364.59 | 2968.82
8102583 | B143 | BP Bluff | 30 Nov 2017 | Chiller is leaking water .. ... | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cleaned out drain evaporator box and unblocked drain., |  | 2 | 750 | 1500 | 0 | , | 60 | 549 | 2049 | 286.86 | 2335.86
8103690 | B143 | BP Kwa Mashu Service Station | 30 Nov 2017 | Walk in chiller is not working -cannot lock door | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Replaced latch and strike lock mechanism on cold drinks chiller., |  | 1 | 483.75 | 483.75 | 950 | Door latch and Strike , | 34 | 311.1 | 1744.85 | 244.28 | 1989.13
8104290 | B143 | New Germany Service Centre | 30 Nov 2017 | Unable to lock freezer room door | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Repaired rear loading door locking mechanism. , |  | 1 | 483.75 | 483.75 | 0 | , | 58 | 530.7 | 1014.45 | 142.02 | 1156.47
8104565 | B143 | BP Northdene | 30 Nov 2017 | Shop air con is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Replaced fan belt and defrost the unit. , |  | 2 | 483.75 | 967.5 | 350 | Fan belt, | 60 | 549 | 1866.5 | 261.31 | 2127.81
8097137 | B143 | Moore Rd Service Station | 2017-09-29 | Refurbishment of air conditioner unit | Reactive Maintenance | Isolate the power to the air conditioning unit and place a lock out tag. Dismantle the complete air conditioner unit and transport to workshop. Strip the entire unit to its basic components and conduct a thorough refurbishment. Prepare and re-gas the unit using R410 gas. Return to site with the refurbished unit and recommission the unit. Conduct a test to ensure that the unit is correctly working. Note: A permit issuer is required to be on site. , |  | 1 | 4920 | 4920 | 3789.98 | Scaffolding (complete with safety signs, guard rails and toe brands), Consumables (Glands, lugs, plugs, joiners, etc), R410 Gas, Foaming Coil Cleaner, | 84 | 714 | 9423.98 | 1319.36 | 10743.34
8104895 | B143 | BP Kwa Mashu Service Station | 30 Nov 2017 | Ice freezer is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Pressure tested and found the unit was short of gas. Topped up with gas. , |  | 2 | 483.75 | 967.5 | 1650 | R404a Gas, | 34 | 311.1 | 2928.6 | 410 | 3338.6
8104704 | B143 | BP Bluff | 30 Nov 2017 | Ice freezer is completely off | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Replaced main breaker on the unit. Tested and found no faults. , |  | 1 | 563 | 563 | 398 | Circuit Breaker , | 60 | 549 | 1510 | 211.4 | 1721.4
8103598 | B143 | Drive In Motors | 30 Nov 2017 | Cold drinks chiller is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cordon off work area, assessed and found the unit condensing and unable to switch on due to a faulty probe. Returned to site, replaced the contactor and HP switch. Pressure tested and found the unit was working fine. , |  | 3 | 483.75 | 1451.25 | 1100 | Contactor 32, HP switch , | 140 | 1281 | 3832.25 | 536.52 | 4368.77
[8 empty] | 23 |  | 16106.75 | 10675.96 |  | 926 | 8396.2 | 35178.91 | 4925.06 | 40103.97