## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8106901 | B151 | BP John Ross | 16 Jan 2018 | Dairy fridge not cooling .. .. .. .. . | Reactive Maintenance | Created safe barricaded work area. Removed old controller and replaced with new to the chiller fridge. Tested chiller to check if working correctly., |  | 2 | 483.75 | 967.5 | 1076 | Controller , | 34 | 311.1 | 2354.6 | 329.64 | 2684.24
8108912 | B151 | BP Bullion Boulevard Express | 16 Jan 2018 | Upright fridge is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Created safe barricaded work area. Cleaned two condenser coils, unblocked and flushed two drain pipes. Tested for normal operation., |  | 1 | 483.75 | 483.75 | 450 | Drain cleaner , Hire of drain rods, | 52 | 475.8 | 1409.55 | 197.34 | 1606.89
8108358 | B151 | Moore Rd Service Station | 17 Jan 2018 | Office air con is leaking water | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Attended to site and found the drains were blocked. Flushed drains with cleaning agent and water. Tested and found no leaks. , |  | 2 | 483.75 | 967.5 | 150 | Drain cleaner, | 52 | 475.8 | 1593.3 | 223.06 | 1816.36
8109218 | B151 | BP Church Street | 17 Jan 2018 | Dairy chiller is leaking water | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found drain pan blocked. Unblocked line and reassemble dairy chiller. , |  | 4 | 563 | 2252 | 0 | , | 174 | 1592.1 | 3844.1 | 538.17 | 4382.27
8108704 | B151 | La Lucia Ridge Oasis | 17 Jan 2018 | Freezer room is not freezing | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found no faults. The freezer room is overloaded causing poor air circulation. Advised the dealer of our findings., |  | 0 | 550 | 0 | 800 | Call out charge , | 0 | 0 | 800 | 112 | 912
8109173 | B151 | BP Northdene | 17 Jan 2018 | Freezer room light not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Removed damaged light fittings and replaced with new. , |  | 2 | 483.75 | 967.5 | 350 | Light fitting , | 60 | 549 | 1866.5 | 261.31 | 2127.81
8108745 | B151 | BP Kwa Mashu Service Station | 17 Jan 2018 | Ice freezer is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Pressured tested and found the unit was short of gas. Topped up gas on the unit. , |  | 1 | 483.75 | 483.75 | 1450 | R404A Gas, | 34 | 311.1 | 2244.85 | 314.28 | 2559.13
8108685 | B151 | BP Waterloo | 17 Jan 2018 | Walk in chiller is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Repaired gas leak and topped up gas. Pressure tested and found no leaks. , |  | 1 | 483.75 | 483.75 | 650 | R22 Gas, | 32 | 292.8 | 1426.55 | 199.72 | 1626.27
8108518 | B151 | La Lucia Ridge Oasis | 17 Jan 2018 | Freezer room is not freezing | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Defrosted coil and adjusted defrost cycle., |  | 1 | 483.75 | 483.75 | 0 | , | 34 | 311.1 | 794.85 | 111.28 | 906.13
8108587 | B151 | Daniels Auto Centre | 17 Jan 2018 | Air con unit is leaking water | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found the unit was leaking from the p-trap. Unblocked and assessed. Quote to install a new drip tray. , |  | 2 | 483.75 | 967.5 | 0 | , | 176 | 1610.4 | 2577.9 | 360.91 | 2938.81
8108618 | B151 | BP West Street | 17 Jan 2018 | Water chiller is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Replaced faulty pressure switch with new. Tested and found no faults. , |  | 1 | 483.75 | 483.75 | 1364 | Pressure switch , | 52 | 475.8 | 2323.55 | 325.3 | 2648.85
8108647 | B151 | BP Raisethorpe | 17 Jan 2018 | Milk/Juice chiller is not cooling | Reactive Maintenance | Created safe barricaded work area. Assessed and discovered chiller short of gas and found oil around chiller coil. Cleaned base of chiller and coil. Topped up unit with gas., |  | 2 | 483.75 | 967.5 | 2450 | R404a gas, | 175 | 1601.25 | 5018.75 | 702.63 | 5721.38
8107632 | B151 | Daniels Auto Centre | 17 Jan 2018 | Clover fridge is leaking .. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cleaned the cabinet and unblocked the drain. , |  | 2 | 483.75 | 967.5 | 150 | Drain cleaner, | 170 | 1555.5 | 2673 | 374.22 | 3047.22
8108171 | B151 | BP Kwa Mashu Service Station | 17 Jan 2018 | Ice freezer room is not freezing | Reactive Maintenance | Created safe barricaded work area. Inspected and discovered ice build up in freezer unit. Defrosted ice build up and adjusted defrost setting., |  | 2 | 483.75 | 967.5 | 0 | , | 30 | 274.5 | 1242 | 173.88 | 1415.88
8109749 | B151 | BP Northdene | 17 Jan 2018 | Dairy chiller ios not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found the unit was short of gas. Topped up R404A gas in the unit and tested. Found no leaks. , |  | 1 | 483.75 | 483.75 | 1250 | R404A Gas, | 60 | 549 | 2282.75 | 319.59 | 2602.34
[8 empty] | 24 |  | 11927 | 10140 |  | 1135 | 10385.25 | 32452.25 | 4543.33 | 36995.58