## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8110589 | B152 | Moore Rd Service Station | 17 Jan 2018 | Freezer room door handle broken | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Opened and repaired freezer room door latch and strike lock. Reinstalled and secured. , |  | 2 | 483.75 | 967.5 | 0 | , | 48 | 439.2 | 1406.7 | 196.94 | 1603.64
8109833 | B152 | BP Kwa Mashu Service Station | 17 Jan 2018 | WBC under bar fridge not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found that the condenser was internally blocked. Stripped unit and clean. Reassembly and secured. , |  | 2 | 483.75 | 967.5 | 0 | , | 34 | 311.1 | 1278.6 | 179 | 1457.6
8109480 | B152 | BP Kwa Mashu Service Station | 17 Jan 2018 | Air con in shop is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found condenser coil blocked. Cleaned coils and filters. , |  | 2 | 483.75 | 967.5 | 175 | Coil cleaner , | 34 | 311.1 | 1453.6 | 203.5 | 1657.1
8110320 | B152 | BP Raisethorpe | 17 Jan 2018 | Cash box air con is leaking | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Found drainage was blocked. Flushed drain with cleaner and water. , |  | 1 | 483.75 | 483.75 | 150 | Drain cleaner, | 170 | 1555.5 | 2189.25 | 306.5 | 2495.75
8110351 | B152 | Araf Fuel Centre | 17 Jan 2018 | Freezer is not freezing .. .. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Washed filters and condenser coil. , |  | 2 | 483.75 | 967.5 | 175 | Coil cleaner , | 52 | 475.8 | 1618.3 | 226.56 | 1844.86
8110463 | B152 | La Lucia Ridge Oasis | 17 Jan 2018 | Freezer room light fitting loose | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Found the light fitting was loose. Re-secured and tested. , |  | 1 | 483.75 | 483.75 | 0 | , | 38 | 347.7 | 831.45 | 116.4 | 947.85
8109843 | B152 | BP West Street | 17 Jan 2018 | Water chiller is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Repaired gas leak and topped up unit with gas. , |  | 2 | 483.75 | 967.5 | 850 | R22 Gas, | 48 | 439.2 | 2256.7 | 315.94 | 2572.64
8109682 | B152 | BP Sibaya | 17 Jan 2018 | Shop air con is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found the unit iced up. Removed all ice build up, washed filters and coils. Checked gas pressure and found the unit was holding pressure. , |  | 1 | 483.75 | 483.75 | 350 | Coil cleaner , | 60 | 549 | 1382.75 | 193.59 | 1576.34
8109675 | B152 | BP Cascades Service Station | 17 Jan 2018 | Freezer room is not freezing | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assesed and found condenser coil blocked. Cleaned coil and adjusted defrost settings. Topped up unit with R404a gas., |  | 2 | 483.75 | 967.5 | 1620 | R404a gas, Cleaning Chemical, | 0 | 0 | 2587.5 | 362.25 | 2949.75
8109676 | B152 | BP Cascades Service Station | 17 Jan 2018 | Dairy chiller is not correct temp | Reactive Maintenance | Assesed and found Dairy chiller not cooling at correct temperature .Re- commisioned chiller, adjusted gas pressure and cleaned condenser., |  | 2 | 483.75 | 967.5 | 1170 | R404a gas, Cleaning chemical, | 185 | 1692.75 | 3830.25 | 536.24 | 4366.49
8109486 | B152 | Drive In Motors | 17 Jan 2018 | Freezer room is not freezing | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and discovered evaporated coil iced. Set the unit to defrost and adjusted defrost settings. Tested unit and it is working fine., |  | 2 | 483.75 | 967.5 | 0 | , | 43 | 393.45 | 1360.95 | 190.53 | 1551.48
8109320 | B152 | BP Waterloo | 17 Jan 2018 | Freezer room is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Found condenser fan motor burnt causing the unit to trip. Disconnected the motor. Returned to site and fitted new single phase fan motor. , |  | 3 | 483.75 | 1451.25 | 2280 | Single phase Ziel fan motor , | 64 | 585.6 | 4316.85 | 604.36 | 4921.21
8109330 | B152 | BP Kwa Mashu Service Station | 17 Jan 2018 | Freezer room is not freezing | Reactive Maintenance | Assessed and tested freezer room unit and discovered freezer room unit was working fine., |  | 0 | 550 | 0 | 800 | Call out charges as agreed., | 0 | 0 | 800 | 112 | 912
[8 empty] | 22 |  | 10642.5 | 7570 |  | 776 | 7100.4 | 25312.9 | 3543.81 | 28856.71