## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8112714 | B156 | Drive In Motors | 30 Jan 2018 | Dairy chiller fan has iced up | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found dairy chiller fan iced up. Defrosted chiller and adjusted settings. Tested unit and it is working well., |  | 1 | 483.75 | 483.75 | 0 | , | 78 | 713.7 | 1197.45 | 167.64 | 1365.09
8112999 | B156 | BP Northdene | 30 Jan 2018 | Dair. y chiller temp too high .. . | Reactive Maintenance | Assessed and found unit tripped on overload. Reset overload and tested all components on unit., |  | 1 | 483.75 | 483.75 | 0 | , | 50 | 457.5 | 941.25 | 131.78 | 1073.03
8112962 | B156 | BP Northdene | 09 Feb 2018 | Dairy chiller is not working .. ..., | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found unit short of gas. Topped up unit with R404a gas. Unit is cooling well., |  | 1 | 750 | 750 | 1250 | R404a gas, | 50 | 457.5 | 2457.5 | 344.05 | 2801.55
8112183 | B156 | Chess Service Station | 09 Feb 2018 | Dairy chiller is leaking water .. ... | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found dairy chiller drain blocked. Unblocked and flushed drain. Tested chiller and is working well., |  | 1 | 563 | 563 | 35 | 40mm Coupling, | 32 | 292.8 | 890.8 | 124.71 | 1015.51
8112167 | B156 | BP Escombe | 09 Feb 2018 | Air con is not working .. .. ... | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found drain blocked. Unblocked and flushed drain. Tested unit and it was working well., |  | 2 | 483.75 | 967.5 | 0 | , | 46 | 420.9 | 1388.4 | 194.38 | 1582.78
8113327 | B156 | La Lucia Ridge Oasis | 09 Feb 2018 | Diary chiller is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found dairy chiller evaporator coil iced up. Defrosted evaporator coil and adjusted defrost settings. Dairy chiller working well., |  | 1 | 483.75 | 483.75 | 0 | , | 28 | 256.2 | 739.95 | 103.59 | 843.54
8112098 | B156 | BP Raisethorpe | 09 Feb 2018 | Dairy chiller temp too high .. ... | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found gas leak on evaporator coil. Removed evvaporator coil to be repaired. Returned to site re-installed repaired evaporator coil. Topped up chiller with R404a gas., |  | 3 | 483.75 | 1451.25 | 1950 | R404a gas, | 348 | 3184.2 | 6585.45 | 921.96 | 7507.41
8112751 | B156 | La Lucia Ridge Oasis | 09 Feb 2018 | Cashier kiosk air con is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found unit short of gas due to unit leaking gas. Repaired gas leak and topped up unit with gas., |  | 1 | 563 | 563 | 1500 | R404a gas, | 22 | 201.3 | 2264.3 | 317 | 2581.3
8112994 | B156 | BP Prospecton Road Service Sta | 09 Feb 2018 | Dairy chiller is not working .. ... ... ... | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found evaporator fan iced up. Defrosted evaporator fan, adjusted defrost setting and defrosted coil.Tested chiller it is working well., |  | 2 | 483.75 | 967.5 | 0 | , | 60 | 549 | 1516.5 | 212.31 | 1728.81
8113068 | B156 | BP Escombe | 09 Feb 2018 | Air con is not working .. ... ... | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found drain blocked. Unblocked and flushed out drain. Tested aircon working well., |  | 1 | 563 | 563 | 150 | Drain rods, | 46 | 420.9 | 1133.9 | 158.75 | 1292.65
8109826 | B156 | BP Escombe | 12 Feb 2018 | Dairy chiller is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found power switch in chiller burnt. Bypassed switch to make chiller work. Temporary repair done. Switch needs to be changed., |  | 1 | 483.75 | 483.75 | 0 | , | 46 | 420.9 | 904.65 | 126.65 | 1031.3
[8 empty] | 15 |  | 7760.25 | 4885 |  | 806 | 7374.9 | 20020.15 | 2802.82 | 22822.97