## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8112194 | B158 | BP Raisethorpe | 09 Feb 2018 | Cash box air con is leaking water | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found drain blocked. Flushed drain, adjusted level on indoor unit and fitted p-trap on drain. Checked unit and there was no leaks., |  | 2 | 483.75 | 967.5 | 0 | , | 174 | 1592.1 | 2559.6 | 358.34 | 2917.94
8113148 | B158 | BP Prospecton Road Service Sta | 09 Feb 2018 | Dairy chiller 2 is not working again | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents.Assessed and found Dairy chiller 2 short of gas. Topped up gas.Tested chiller working well, |  | 2 | 563 | 1126 | 650 | R22 Gas, | 60 | 549 | 2325 | 325.5 | 2650.5
8113370 | B158 | Drive In Motors | 12 Feb 2018 | Dairy chiller is not working .. ... ... | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found condenser coil blocked with sand. Cleaned condensor coil and topped up unit with gas. Tested unit and is cooling well., |  | 1 | 563 | 563 | 1650 | R404a gas, | 76 | 695.4 | 2908.4 | 407.18 | 3315.58
8112963 | B158 | BP Northdene | 12 Feb 2018 | No power to freezer .. .. .. .. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found freezer working. Checked all components and all is fine. Store experienced power failure., |  | 0 | 563 | 0 | 800 | Call out charge , | 0 | 0 | 800 | 112 | 912
8113775 | B158 | BP Bluff | 12 Feb 2018 | Office air con is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found compressor overheated and unit has a gas leak. Repaired gas leak, cooled condenser and topped up unit with gas. Tested unit and it is cooling well., |  | 3 | 483.75 | 1451.25 | 450 | R22 Gas, | 52 | 475.8 | 2377.05 | 332.79 | 2709.84
8113852 | B158 | Moore Rd Service Station | 12 Feb 2018 | Freezer room has no power | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assesed and found freezer room condenser fan motor needs to be replaced. Removed damaged condenser fan motor and replaced with new. Tested the unit and is working well., |  | 3 | 483.75 | 1451.25 | 580 | 34W fan motor, | 36 | 329.4 | 2360.65 | 330.49 | 2691.14
8113539 | B158 | Westville Autohouse | 12 Feb 2018 | Walk in chiller temp too high | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found chiller is leaking and condenser fan motor needs to be replaced. Repaired leak on chiller and topped up with gas. Returned to site with condensor fan motor. Removed and replaced condensor fan motor with new and adjusted cycle fan. Tested chiller and is working well., |  | 2 | 483.75 | 967.5 | 3600 | Bottle Disposable R22a Gas, Condenser 350MM Fan motor , | 76 | 695.4 | 5262.9 | 736.81 | 5999.71
8113882 | B158 | La Lucia Ridge Oasis | 12 Feb 2018 | Dairy chiller temp too high .. ... | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found dairy chiller short of gas due to a leak. Repaired gas leak and topped up the unit with gas. Tested the chiller and it is cooling well., |  | 1 | 563 | 563 | 1000 | R22 Gas, | 12 | 109.8 | 1672.8 | 234.19 | 1906.99
8111884 | B158 | Chess Service Station | 12 Feb 2018 | Freezer room door handle broken | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found freezer room door handle broken. Re-secured door handle and door hinge. Tested door and is working well., |  | 1 | 563 | 563 | 0 | , | 32 | 292.8 | 855.8 | 119.81 | 975.61
8112961 | B158 | BP Northdene | 12 Feb 2018 | Shop air con is not working .. ... ... | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found aircon is working correctly and cooling well., |  | 1 | 563 | 563 | 0 | , | 50 | 457.5 | 1020.5 | 142.87 | 1163.37
8114296 | B158 | BP Escombe | 12 Feb 2018 | Dairy chiller is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Isolated power supply to chiller unit. Assessed and repaired burnt wiring in dairy chiller. Replaced burnt power switch. Tested unit and it is cooling well., |  | 1 | 483.75 | 483.75 | 235 | Power switch, | 46 | 420.9 | 1139.65 | 159.55 | 1299.2
8110857 | B158 | BP Bullion Boulevard Express | 14 Feb 2018 | Air con in the office is leaking water | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found aircon drip tray full of water. Cleaned drip tray filters and tested unit it is cooling well., |  | 2 | 483.75 | 967.5 | 0 | , | 52 | 475.8 | 1443.3 | 202.06 | 1645.36
[8 empty] | 19 |  | 9666.75 | 8965 |  | 666 | 6093.9 | 24725.65 | 3461.59 | 28187.24