## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8117607 | B170 | BP Northdene | 15 Mar 2018 | 10 x lights are not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found globes and ballasts needs to be replaced. Removed non working globes and ballasts and replaced with new. Tested and it is working well., |  | 2 | 483.75 | 967.5 | 690 | Light bulbs, Ballasts, | 50 | 457.5 | 2115 | 296.1 | 2432.25
8117725 | B170 | BP Northdene | 19 Mar 2018 | Walk in freezer is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found drain blocked. Unblocked drain and tested unit it is cooling well., |  | 1 | 483.75 | 483.75 | 0 | , | 50 | 457.5 | 941.25 | 131.775 | 1082.44
8117925 | B170 | BP Raisethorpe | 19 Mar 2018 | Stripped out unit, flushed out internal drain and cleaned drip tray MTC: | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and stripped unit. Discovered internal drain and drip tray needs to be cleaned. Flushed out internal drain and cleaned drip tray. Assembled unit and tested it is cooling well., |  | 1 | 483.75 | 483.75 | 0 | , | 174 | 1592.1 | 2075.85 | 290.619 | 2387.23
8118290 | B170 | BP Waterloo | 04 Apr 2018 | Dairy chiller is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found controller faulty. Controller and sensors need to be ordered. Returned to site and removed damaged controller and PTC sensors and replaced with new. Rewired unit to suit and tested unit it is working well., |  | 4 | 483.75 | 1935 | 1444 | Controller 214 , PTC sensor, | 40 | 366 | 3745 | 561.75 | 4306.75
8119390 | B170 | BP Edendale Service Station | 04 Apr 2018 | Walk in chiller lights not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found chiller lights not working. Isulated wiring on freezer room door frame. Restored breaker and tested lights and it is working well., |  | 2 | 563 | 1126 | 0 | , | 182 | 1665.3 | 2791.3 | 418.695 | 3210
8120087 | B170 | BP Northdene | 04 Apr 2018 | Freezer room is not working | Reactive Maintenance | Tested and and found evertything working okay in freezer room., |  | 0 | 550 | 0 | 800 | Call out charges as Agreed, | 0 | 0 | 800 | 120 | 920
8117591 | B170 | Moore Rd Service Station | 04 Apr 2018 | Air con is not cooling .. .. ... ... | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found unit short of gas. Needed a permit issuer on site as we nneded to check unit on roof to detect leak. Returned to site and found gas leak on valve. Repaired leak and topped up unit with gas. Tested unit and it is cooling well., |  | 5 | 483.75 | 2418.75 | 2414.39 | R404 gas, | 76 | 695.4 | 5528.54 | 829.281 | 6357.82
8118382 | B170 | BP Dube Village Mall | 05 Apr 2018 | Cold drinks fridge is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found unit had no gas. A gas leak was found at the oil separator. Topped up unit with gas temporarily and ordered new oil separator., Returned to site with new oil separator. Removed old oil separator from unit and replaced with new oil separator. Topped up unit with gas. Tested unit and it is cooling well., |  | 7 | 563 | 3544.75 | 4455.9 | R404a gas, Oil Separator unit, | 88 | 805.2 | 8805.85 | 1320.8775 | 10126.73
8115206 | B170 | Daniels Auto Centre | 10 Apr 2018 | Air con leaking in shop-to install drip tray | Reactive Maintenance | Created a safe barricaded work area. Removed old drip tray and installed a prefabricated galvanized drip tray with an allowance for drainage to the outside of the building. Cleaned work area and made safe., |  | 5 | 483.75 | 2418.75 | 4912.46 | Drain pipe, Brackets, Galvanize Drip Tray, | 168 | 1537.2 | 8868.41 | 1330.2615 | 10198.67
8118093 | B170 | BP Escombe | 12 Apr 2018 | 4 x glass chiller is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found controller faulty. Replaced controller and topped unit up with gas. Returned to site and replaced old thermostat with new. Tested unit it is working well., |  | 6 | 483.75 | 2902.5 | 4445.08 | ERC 211 controller, R404a gas, UT 72 Thermostat, | 0 | 0 | 7347.58 | 1102.137 | 8449.72
8119758 | B170 | New Germany Service Centre | 12 Apr 2018 | Dairy chiller is leaking water | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found drain blocked. Unblocked drain and tested drainage it is working well., |  | 1 | 483.75 | 483.75 | 0 | , | 44 | 402.6 | 886.35 | 132.9525 | 1019.3
8120757 | B170 | BP Escombe | 13 Apr 2018 | 4 glass door chiller is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found electrical isolator cover broken causing waterto get into unit resulting in unit tripping. Secured cover and electrician to replace isolator box. , |  | 3 | 750 | 2250 | 0 | , | 46 | 420.9 | 2670.9 | 400.635 | 3071.54
[8 empty] | 37 |  | 19014.5 | 19161.83 |  | 918 | 8399.7 | 46576.03 | 6935.0835 | 53562.45