## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8122259 | B176 | Umlazi Service Centre | 30 Apr 2018 | Dairy chiller is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found condensor coil blocked. Stripped and cleaned coil. Reset unit and checked gas all is good. Tested unit and it is working correctly. , |  | 2 | 563 | 1126 | 0 | , | 60 | 549 | 1675 | 251.25 | 1926.25
8124946 | B176 | 222 Service Station | 04 May 2018 | Walk in fridge and chiller are not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found condensor needs to be cleaned on two fridges. Cleaned and serviced condensors. Checked and found phase missing on chiller. Replaced sneider contactor and topped up unit with gas. Tested unit it is cooling well., |  | 2 | 483.75 | 967.5 | 3650 | R404a gas, Sneider contactor, | 58 | 530.7 | 5148.2 | 772.23 | 5920.43
8124831 | B176 | Bullion Boulevard Express | 04 May 2018 | Office air con is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found electrics faulty. Rectified faulty electrics. Stripped and cleaned drip tray. tested unit it is working correctly., |  | 2 | 483.75 | 967.5 | 0 | , | 326 | 2982.9 | 3950.4 | 592.56 | 4542.96
8125042 | B176 | BP Northdene | 07 May 2018 | Chiller unit temp too high | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found unit on defrost cycle. Waited for it to come out of defrost mode and it is working well, |  | 2 | 483.75 | 967.5 | 0 | , | 50 | 457.5 | 1425 | 213.75 | 1638.75
8125105 | B176 | BP Ridge Oasis | 07 May 2018 | Walk in freezer fan not working and unit tripped | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found armour flex broken, evaporator fan motor seized and thermostat needs replacing. Replaced evaporator fan motor and thermostat. Removed broken armourflex and replaced with new. Tested unit and it is cooling well., |  | 1 | 563 | 563 | 3170 | Fan Motor 300mm, 5/8 Armorflex, Thermostat, | 100 | 915 | 4648 | 697.2 | 5345.2
8125100 | B176 | Drive In Motors | 07 May 2018 | Managers office air con not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Checked and found unit short of gas due to gas leak. Repaired gas leak and topped unit with gas. Tested aircon unit and cooling well., |  | 1 | 483.75 | 483.75 | 900 | R410a gas, | 76 | 695.4 | 2079.15 | 311.8725 | 2391.02
8125322 | B176 | BP Berea E L | 08 May 2018 | Convenience chiller is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found unit tripping. Reset unit. Cleaned condensor and found condensor fan needs to be replaced. Replaced condensor fan and topped unit with gas. Tested unit and it is cooling well., |  | 3 | 483.75 | 1451.25 | 2775 | 350 mm condensor fan , R404 gas, | 42 | 384.3 | 4610.55 | 691.5825 | 5302.13
8125323 | B176 | BP Chatsworth Circle | 08 May 2018 | Walk in fridge not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found condensor coil blocked. Washed out condensor coil and adjusted gas pressures. Topped up unit with gas. Tested and unit is cooling well., |  | 2 | 483.75 | 967.5 | 900 | R404a gas, | 66 | 603.9 | 2471.4 | 370.71 | 2842.11
8117806 | B176 | Araf Fuel Centre | 09 May 2018 | Office air con is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found condensor fan blade needs to be replaced. Removed damaged blade and installed new fan blade. Tested unit it is working correctly., |  | 1 | 483.75 | 483.75 | 330 | Condensor fan blade, | 44 | 402.6 | 1216.35 | 182.4525 | 1398.8
8126219 | B176 | Araf Fuel Centre | 16 May 2018 | milk chiller is not working. milk is getting off | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found compressor sump heater cable burnt. Removed compressor sump heater cable and replaced with new. Tested unit and it is cooling well., |  | 1 | 563 | 563 | 0 | , | 44 | 402.6 | 965.6 | 144.84 | 1110.44
8126168 | B176 | BP Bluff | 16 May 2018 | Wild bean freezer not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found gas leak on unit. Repaired gas leak and topped up unit with gas. Tested unit and it is cooling well., |  | 1 | 483.75 | 483.75 | 3600 | R404a gas, | 52 | 475.8 | 4559.55 | 683.9325 | 5243.48
8126326 | B176 | BP Church Street | 16 May 2018 | Dairy chiller is not working properly | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found condensor blocked. Cleaned out condensor and adjusted temperature on thermostat. Tested unit it is cooling well., |  | 1 | 483.75 | 483.75 | 0 | , | 170 | 1555.5 | 2039.25 | 305.8875 | 2345.14
8124440 | B176 | BP West Street | 16 May 2018 | Water chiller is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found unit leaking gas. Repaired gas leak and topped unit with gas. Tested unit and it is cooling well., |  | 2 | 483.75 | 967.5 | 1000 | R22 gas, | 20 | 183 | 2150.5 | 322.575 | 2473.08
8124000 | B176 | BP Bullion Boulevard Express | 16 May 2018 | Office air con is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found unit has no 220v power supply. DB Board was locked out., |  | 2 | 563 | 1126 | 0 | , | 326 | 2982.9 | 4108.9 | 616.335 | 4725.24
8123157 | B176 | BP West Street | 16 May 2018 | Drinks chiller light sare not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found chiller light not working. Removed and replaced with new one 58w ballast and tube. Tested light and it is working correctly., |  | 2 | 563 | 1126 | 475 | Ballast 58 watt, 58 watt tube, | 20 | 183 | 1784 | 267.6 | 2051.6
8126479 | B176 | BP Verulam | 17 May 2018 | Dairy chiller is making a loud noise | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found timer switch and fan motor needs to replaced. Replaced fan motor and timer on unit. Defrosted coil. Tested unit and it is cooling well., |  | 2 | 563 | 1126 | 1694 | Legrand timer switch, 16W Fan Motor, | 40 | 366 | 3186 | 0 | 3186
8126446 | B176 | BP Northdene | 17 May 2018 | abi chiller lights not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found two light tubes and ballast needs to be replaced. Replaced light tubes and ballast. Tested chiller lights and it is working correctly., |  | 1 | 483.75 | 483.75 | 190 | 58w tubes, 58w Ballast, | 50 | 457.5 | 1131.25 | 169.6875 | 1300.94
8126007 | B176 | La Lucia Ridge Oasis | 23 May 2018 | Dairy chiller is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found thermostat,timer switch and contactor needs to be changed. Stripped unit and removed faulty parts. Replaced thermostat, timer switch and contactor. Tested unit and it is cooling well., |  | 2 | 563 | 1126 | 2874 | Legrand timer switch, UT 72 Thermostat, Contactor, | 10 | 91.5 | 4091.5 | 613.725 | 4705.23
8118916 | B176 | BP West Street | 23 May 2018 | Shop air con is not cooling | Reactive Maintenance | Created a safe barricaded work area. Isolated power to the air conditioning unit. Supplied and installed a new PC board and 2 new fan motors. Recommissioned the unit and conducted a test to ensure that the unit is functioning correctly. Cleaned and made work area safe. , |  | 7 | 483.75 | 3386.25 | 7206 | PC Board, Fan Motor, | 44 | 402.6 | 10994.85 | 1649.2275 | 12644.08
8123975 | B176 | BP Waterloo | 23 May 2018 | Air con is leaking water | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found aircon leaking due to drain being blocked. Unblocked drain and checked no water leaking on unit., |  | 1 | 750 | 750 | 0 | , | 40 | 366 | 1116 | 167.4 | 1283.4
8124054 | B176 | BP Prospecton Road Service Sta | 23 May 2018 | Dairy chiller no 2 is tripping | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Checked and found burnt wiring on compressor control box. Repaired burnt wiring and replaced one condensor fan motor that was burnt. Tested unit and it is cooling well. , |  | 3 | 563 | 1689 | 650 | Condensor fan motor, | 60 | 549 | 2888 | 433.2 | 3321.2
8123640 | B176 | Araf Fuel Centre | 23 May 2018 | Cashie kiosk air con is leaking water | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found no fault., |  | 0 | 550 | 0 | 800 | Call out charges as Agreed, | 0 | 0 | 800 | 120 | 920
[8 empty] | 41 |  | 21288.75 | 30214 |  | 1698 | 15536.7 | 67039.45 | 9578.0175 | 76617.48