## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8126804 | B184 | BP Umbilo | 22 May 2018 | Aircon outlet grids needs cleaning and servicing | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cleaned diffuses and grills on aircon unit. To return to replace 3 diffuses. Returned to site and installed 3 new diffuses on shop floor. Tested unit and it is working well., |  | 7 | 483.75 | 3386.25 | 2845 | Filter Media cloth, Diffuser, Clear tape, | 60 | 549 | 6780.25 | 1017.0375 | 7797.29
8127229 | B184 | BP John Ross | 22 May 2018 | keeps on tripping on DV Board and at compressor. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found unit tripping when on defrost mode. Tested and found drain pan heater faulty. Disconnected drain pan heater and to return to site to replace. Returned to site and replaced drain pan heater with new. Tested unit and it is working well., |  | 5 | 483.75 | 2418.75 | 710 | Drain pan heater, | 630 | 5764.5 | 8893.25 | 1333.9875 | 10227.24
8129597 | B184 | BP Kwa Mashu Service Station | 07 Jun 2018 | Deep freezer compressor is covered by ice build up | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found drain heater needs to be replaced. Removed excess ice from freezer, |  | 1 | 483.75 | 483.75 | 0 | , | 22 | 201.3 | 685.05 | 102.7575 | 787.81
8129987 | B184 | BP Kwa Mashu Service Station | 12 Jun 2018 | Deep freezer compressor is covered by ice build up | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Removed excess ice from freezer. Checked and found drain heater damaged. Replaced damaged drain heater and tested unit it is working well., |  | 1 | 563 | 563 | 620 | Drain heater, | 22 | 201.3 | 1384.3 | 207.645 | 1591.95
8130108 | B184 | BP Northdene | 12 Jun 2018 | Dairy chiller temp too high | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and repaired gas leak. Topped up unit with gas. Tested unit and it is cooling well., |  | 1 | 483.75 | 483.75 | 1800 | R404a gas, | 50 | 457.5 | 2741.25 | 411.1875 | 3152.44
8130286 | B184 | BP Bluff | 13 Jun 2018 | Fruit and veg chiller is leaking | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and repaired water leak on chiller. Tested chiller and it is working correctly., |  | 1 | 483.75 | 483.75 | 0 | , | 56 | 512.4 | 996.15 | 149.4225 | 1145.57
8130609 | B184 | BP Arena Park | 18 Jun 2018 | walk in chiller making a loud noise | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found fan motor seized. Removed faulty fan motor and replaced with new. Tested unit it is working correctly., |  | 2 | 563 | 1126 | 2500 | Fan Motor 300mm EBM, | 68 | 622.2 | 4248.2 | 637.23 | 4885.43
8130632 | B184 | BP Ridge Oasis | 18 Jun 2018 | Main shop air con is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found aircon unit unit tripped on P3 error code. Reset error code on unit main PC Board. Tested unit it is cooling well., |  | 2 | 563 | 1126 | 0 | , | 102 | 933.3 | 2059.3 | 308.895 | 2368.2
8130831 | B184 | BP Chatsworth Circle | 18 Jun 2018 | Freezer is not working -possibly lights | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found that light tubes and ballasts need replacing. Replaced two light tubes and one ballast. Tested lights in freezer and it is working correctly., |  | 1 | 483.75 | 483.75 | 570 | 58w tubes, Ballast 58 watt, | 66 | 603.9 | 1657.65 | 248.6475 | 1906.3
8131038 | B184 | BP Chatsworth Circle | 21 Jun 2018 | Air con is not working -not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found aircon unit tripped. Reset unit and tested it is working well., |  | 1 | 483.75 | 483.75 | 0 | , | 66 | 603.9 | 1087.65 | 163.1475 | 1250.8
8128603 | B184 | Palm Service Centre | 25 Jun 2018 | Install new compressor as per quote. | Reactive Maintenance | Created a safe barricaded work area. Isolated the power to the dairy fridge. Supplied and installed a new compressor and drier. Prepared and recharged the unit using R404a gas. Recommissioned and conducted a test to ensure that the dairy fridge is correctly functioning., |  | 6 | 483.75 | 2902.5 | 13848.13 | Drier, Compressor, R404a Gas, | 120 | 1098 | 17848.63 | 2677.2945 | 20525.92
8130853 | B184 | BP Bullion Boulevard Express | 25 Jun 2018 | The Dairy Chillers shelve is falling off we cannot put stock on it or the shelve back in the chiller. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Repaired dairy shelve that was broken. Installed and resecured shelve onto fridge., |  | 1 | 563 | 563 | 0 | , | 58 | 530.7 | 1093.7 | 164.055 | 1257.76
[8 empty] | 29 |  | 14504.25 | 22893.13 |  | 1320 | 12078 | 49475.38 | 7421.307 | 56896.71