## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8133656 | B190 | BP Northdene | 11 Jul 2018 | shelves in freezer is broken | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Repaired broken shelving in freezer room., |  | 1 | 483.75 | 483.75 | 0 | , | 50 | 457.5 | 941.25 | 141.1875 | 1082.44
8134299 | B190 | La Lucia Ridge Oasis | 16 Jul 2018 | dairy chiller temperature is high .....Urgent | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found unit icing up. Adjusted defrost timer thermostat. Replaced legrand timer. Tested unit and it is cooling correctly., |  | 2 | 563 | 1126 | 844 | Legrand timer switch, | 10 | 91.5 | 2061.5 | 309.225 | 2370.73
8134223 | B190 | BP Cascades Service Station | 16 Jul 2018 | drinks Chiller door lights(3) not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found tubes and electronic ballast needs to be replaced. Replaced 2 tubes and a electronic ballast. Tested chiller lights and it is working well. , |  | 2 | 483.75 | 967.5 | 570 | Ballast 58 watt, 58w tubes, | 176 | 1610.4 | 3147.9 | 472.185 | 3620.09
8134522 | B190 | BP Raisethorpe | 17 Jul 2018 | Dairy chiller is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found unit leaking gas. Repaired gas leak, defrosted coils and cleaned them. Topped up unit with gas and tested unit it is cooling well., |  | 3 | 563 | 1689 | 2520 | R404 gas, Cleaning chemical, | 174 | 1592.1 | 5801.1 | 870.165 | 6671.27
8134521 | B190 | BP Escombe | 17 Jul 2018 | Dairy Chiller making a loud noise | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found two condensor fan motors needs to be replaced. Removed damaged fan motors and replaced with new. Tested unit and it is working well., |  | 2 | 563 | 1126 | 1300 | 16W Fan Motor, | 62 | 567.3 | 2993.3 | 448.995 | 3442.3
8134455 | B190 | BP Ridge Oasis | 17 Jul 2018 | The Big walk in freezer - the drain pipe is leaking onto the floor | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found bloer coil damaged and needs replacement. Temporary repaired unit to quote for new coil blower., |  | 1 | 563 | 563 | 0 | , | 106 | 969.9 | 1532.9 | 229.935 | 1762.84
8134704 | B190 | BP Umbilo | 18 Jul 2018 | Dairy fridge is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed unit and found unit short of gas. Topped up unit with gas and adjusted expansion valve. Tested unit and it is working correctly., |  | 1 | 483.75 | 483.75 | 1000 | R22 gas, | 40 | 366 | 1849.75 | 277.4625 | 2127.21
8134951 | B190 | BP Waterloo | 20 Jul 2018 | Walk in freezer is needin attention | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and defrosted blower coils. Tested and found timer faulty and needs replacing. Returned to site and replaced timer and adjusted thermostat. Tested unit and it is cooling well, |  | 3 | 483.75 | 1451.25 | 844 | Legrand timer switch, | 80 | 732 | 3027.25 | 454.0875 | 3481.34
8135245 | B190 | BP Verulam | 23 Jul 2018 | Dairy fridge has a lot of ice build up and is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found evaporator coil iced up. Defrosted coil and found contactor needs to be replaced. Replaced damaged contactor with new. Tested unit and it is working correctly., |  | 2 | 483.75 | 967.5 | 780 | Contactor, | 40 | 366 | 2113.5 | 317.025 | 2430.53
8135386 | B190 | BP Verulam | 24 Jul 2018 | Shop air con is leaking water on shop floor | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found no fault on Aircon, |  | 0 | 483.75 | 0 | 800 | Call out charges as Agreed, | 0 | 0 | 800 | 120 | 920
8135404 | B190 | Palm Service Centre | 24 Jul 2018 | WBC Freezer Door latch is not closing / locking | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found freezer door latch broken. Repaired door latch and it is working well., |  | 2 | 483.75 | 967.5 | 0 | , | 60 | 549 | 1516.5 | 227.475 | 1743.98
8135690 | B190 | Chess Service Station | 26 Jul 2018 | Shop air con is not working properly | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found filters blocked. Removed filters from unit and cleaned them. Fitted filters back and tested unit it is cooling well., |  | 2 | 563 | 1126 | 0 | , | 32 | 292.8 | 1418.8 | 212.82 | 1631.62
8135903 | B190 | BP Bullion Boulevard Express | 30 Jul 2018 | The walk in freezer is not freezing | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and reprogrammed dantoss controller for defrost settings. Tested unit and it is working correctly., |  | 2 | 483.75 | 967.5 | 0 | , | 58 | 530.7 | 1498.2 | 224.73 | 1722.93
8135317 | B190 | BP Sibaya | 01 Aug 2018 | Freezer room is not freezing | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found expansion valve not regulating correctly. Temporary repair done to system to return to site to replace valve., Returned to site replaced damaged expansion valve with new. Topped up unit with gas. Tested unit it is working correctly., |  | 3 | 563 | 1530.5 | 3100 | Expansion Valve, R404a gas, | 68 | 622.2 | 5252.7 | 787.905 | 6040.61
[8 empty] | 26 |  | 13449.25 | 11758 |  | 956 | 8747.4 | 33954.65 | 5093.1975 | 39047.89