## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8055960 | B27 | Palm Service Centre | 07 Nov 2016 | Office air con is leaking | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Stripped unit and cleaned out drip tray. , |  | 1 | 375 | 375 | 0 | , | 60 | 510 | 885 | 123.9 | 1008.9
8057127 | B27 | BP John Ross | 13 Nov 2016 | Walk in freezer all freezing up | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed work and found that the heater to be faulty. Returned, found the entire drip tray iced up. Defrost ice and replaced faulty drain heater. Repaired the drain. Returned and found the unit tripped out on the overload. Reset the overload to 5A from 4A and assessed operation. , Sunday Labour, |  | 6 | 2475 | 375 | 425 | Heater tape 6ft, | 126 | 1071 | 3971 | 555.94 | 4526.94
8057498 | B27 | BP Verulam | 15 Nov 2016 | Dairy fridge leaking water onto floor | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Attended to site but was informed by the manager to return to site the next day. Returned and found that the drain was leaking. Sealed the drain with silicone. Adjusted the defrost timer. , |  | 2 | 750 | 375 | 52 | Silicone , | 68 | 578 | 1380 | 193.2 | 1573.2
8057635 | B27 | BP Ridge Oasis | 16 Nov 2016 | Shop air con is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found that an issuer will be required to access the roof. Returned to site and erected mobile tower scaffold. Defrost the ice build up and re-gassed the unit. , |  | 3 | 1125 | 0 | 1400 | R410 Gas, | 240 | 2040 | 4565 | 639.1 | 5204.1
8057666 | B27 | BP Northdene | 16 Nov 2016 | Dairy chiller on + 8 | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cordon off work area and repaired gas leak. Topped up with gas. Washed and cleaned condenser coils. Pressure tested the unit and found no leaks. , |  | 2 | 750 | 375 | 1200 | Gas, | 60 | 510 | 2460 | 344.4 | 2804.4
8057811 | B27 | Moore Rd Service Station | 17 Nov 2016 | Aircon in Cashiers Booth leaking water profusely. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cordon off work area to make safe. Unblocked the drain. Tested and found no blockage., |  | 1 | 375 | 375 | 0 | , | 52 | 442 | 817 | 114.38 | 931.38
8057924 | B27 | Chess Service Station | 18 Nov 2016 | Shop air con is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cordon off work area to make safe. Cleaned the filters. Issuer is required to get onto the roof. Returned to site and washed outdoor coils and filers. Defrost and removed ice build up. Replaced damaged suction line valve. Re-gassed the unit and tested. Found no leaks. Had to return. Readjusted and secured the v-belts. Defrost the coils and monitored., |  | 10 | 3750 | 375 | 1275 | R407 Gas, Suction line valve and fittings , | 156 | 1326 | 6351 | 889.14 | 7240.14
8058064 | B27 | BP Sibaya | 21 Nov 2016 | WBC walk in freezer -fan icing up | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found that the stock was obstructing air flow. Rearranged the stock accordingly. , |  | 1 | 375 | 375 | 0 | , | 60 | 510 | 885 | 123.9 | 1008.9
8058196 | B27 | BP Dube Village Mall | 21 Nov 2016 | Shop floor air con is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found filters to be blocked. Cleaned and washed dirty filters., |  | 2 | 750 | 375 | 0 | , | 52 | 442 | 1192 | 166.88 | 1358.88
8058264 | B27 | BP Arena Park | 22 Nov 2016 | Walk in fchiller fan icing up | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cordon off work area to make safe. Defrost and cleaned coils. Replaced damaged pressure switch. Re-gassed the unit and adjusted the temperature. , |  | 4 | 1500 | 375 | 1345 | R22 Gas, Pressure switch , | 60 | 510 | 3355 | 469.7 | 3824.7
8058299 | B27 | Umlazi Service Centre | 22 Nov 2016 | Walk in chiller fan making a loud grinding noise | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Made work area safe and assessed. Removed damaged fan motors to dispose. Replaced with new and tested. , |  | 2 | 750 | 0 | 2400 | Fan motor, | 64 | 544 | 3694 | 517.16 | 4211.16
8058448 | B27 | BP Raisethorpe | 23 Nov 2016 | Juice chiller is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Made work area safe and conducted an assessment. Replaced damaged sensor cable with new. Monitored and tested the unit. , |  | 3 | 1125 | 375 | 156 | Cable, | 220 | 1870 | 3151 | 441.14 | 3592.14
8058512 | B27 | BP Arena Park | 24 Nov 2016 | Chiller not working. water is leaking | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Sealed screws with silicone where leak was detected. Checked drain outlet for blockage. Monitored unit temperature. Condensation on outside of fridge doors caused due poor performance of shop aircon., |  | 3 | 1125 | 375 | 59 | Silicone , | 60 | 510 | 1694 | 237.16 | 1931.16
8058576 | B27 | Moore Rd Service Station | 24 Nov 2016 | Air con in office leaking profusely | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Unblocked the drain and flushed the line. , |  | 2 | 750 | 375 | 0 | , | 38 | 323 | 1073 | 150.22 | 1223.22
8058630 | B27 | Umlazi Service Centre | 24 Nov 2016 | walk in freezer leaking water in too pie stock and get damaged, plus theres a pool of water sipping to the shop floor now fro freezer. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Made work area safe and assessed. Found 2 leaks on the valves. Repaired the leaks and re-gassed the unit. Unblocked condensate drain and main drain outlet. Sealed inside of the freezer with silicone. Replaced corroded drain pipe with new copper pipe and fittings. Cleaned coils. , |  | 6 | 2250 | 375 | 2089 | R404 Gas , Coil cleaner , Copper pipe and fittings , Silicone , Tread tape, flux, gloves , | 64 | 544 | 4883 | 683.62 | 5566.62
8058672 | B27 | BP Ridge Oasis | 25 Nov 2016 | Chiller unit tripping on the unit | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cordon off work area to make safe. Replaced 2x defective fan motor with new. Tested system and, |  | 3 | 1125 | 375 | 2400 | Fan motor, | 110 | 935 | 4460 | 624.4 | 5084.4
8058886 | B27 | BP Arena Park | 26 Nov 2016 | Chiller lights stopped working since shutdown | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found that the breaker was down. Reset the breaker and tested. Found no faults. , |  | 1 | 375 | 375 | 0 | , | 60 | 510 | 885 | 123.9 | 1008.9
8058939 | B27 | La Lucia Ridge Oasis | 28 Nov 2016 | Chiller fridge not working and stock is melting-high temperature | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed the unit. Defrost evaporator coils. Repositioned the thermostat sensor probe., |  | 3 | 1125 | 375 | 0 | , | 30 | 255 | 1380 | 193.2 | 1573.2
8058947 | B27 | BP Ridge Oasis | 28 Nov 2016 | Day freezer not getting down to right temp | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found a gas leak on the suction valve. Repaired the valve. Topped up with gas. Replaced orifice. Pressure tested and found no leaks, |  | 4 | 1500 | 375 | 1645 | Orifice, R404 Gas , | 120 | 1020 | 4165 | 583.1 | 4748.1
8058990 | B27 | BP Arena Park | 28 Nov 2016 | Walk in freezer not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cordon off work area to make safe. Replaced defective outdoor condenser fan motor with new. Tested system and assessed gas limits. , |  | 3 | 1125 | 375 | 1200 | Fan motor, | 60 | 510 | 2835 | 396.9 | 3231.9
8058991 | B27 | BP Arena Park | 28 Nov 2016 | Temp gauge is showing incorrect temp | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Made work area safe. Defrost and clean evaporator coils. Replaced the damaged thermostat with new and adjusted temperature settings accordingly. , |  | 3 | 1125 | 375 | 895 | Thermostat , | 0 | 0 | 2020 | 282.8 | 2302.8
8059127 | B27 | BP Arena Park | 28 Nov 2016 | Shop[ air con is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed the unit and re-gassed. Adjusted the v-belt tension. Washed the coils and cleaned the fan housing. , |  | 3 | 1125 | 375 | 1379 | R22 Gas, Coil cleaner , | 60 | 510 | 3014 | 421.96 | 3435.96
[8 empty] | 68 |  | 7500 | 17920 |  | 1820 | 15470 | 59115 | 8276.1 | 67391.1