## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8047657 | B52 | BP Ridge Oasis | 26 Aug 2016 | Extractor fan in public toilets keeps tripping the circuit breakers at the DB. 3 Phase. | Reactive Maintenance | Upon inspection, it was found that the motor for the extractor fan to be in a state of dead short. We are to isolate and remove the defective unit and replace the extractor fan unit only. Re-connect the new fan and conduct a test to ensure the new unit is functioning correctly. , |  | 3 | 325 | 975 | 6570 | Extractor fan - 400 cfm, Scaffolding complete with safety signs, guard rails and toe boards, Consumables , | 40 | 340 | 7885 | 1103.9 | 8988.9
8057392 | B52 | Araf Fuel Centre | 15 Nov 2016 | Freezer is running on +5 it should be -18 | Reactive Maintenance | Upon inspection, a non-repairable internal leak was found as it is a closed unit. Isolate the damaged freezer, remove existing damaged unit and replace with new. Restore power and conduct a test to ensure the new unit is functioning correctly. Clean and make safe. , |  | 2 | 375 | 750 | 40728.26 | Upright freezer, Consumables, Transportation, | 46 | 391 | 41869.26 | 5861.7 | 47730.96
8058199 | B52 | BP Verulam | 21 Nov 2016 | 2 x shop air cons not working | Reactive Maintenance | Isolate the power to the affected fan motor and unit. Remove and replace the damaged fan motor with new. Calibrate the remote and sensor for the second air con unit. Reconnect power and conduct a test to ensure the equipment is functioning correctly. Clean and make safe., |  | 2 | 375 | 750 | 9146.53 | Consumables, Calibrate remote and sensor , Fan Motor, | 80 | 680 | 10576.53 | 1480.71 | 12057.24
8063983 | B52 | BP West Street | 12 Jan 2017 | All air cons not working-shop and offices | Reactive Maintenance | Cordon off the work area complete with safety cones, danger tape and warning signs. Isolate power to the chiller unit and place a lockout tag on the DB. Disconnect and remove the mother board, power board and control board. Install a new mother board, power board and control board. Prepare and re-gas the chiller unit. Re-wire and connect the new components. Remove lockout tag and turn power on. Conduct a test to insure that the chiller unit to operating correctly. Clean and make work area safe., |  | 8 | 375 | 3000 | 6640.74 | Electronic PCB control unit , Receiver sensor , Receiver unit , Consumables, Scaffolding complete with safety signs, guard rails and toe boards, | 44 | 374 | 10014.74 | 1402.06 | 11416.8
8066037 | B52 | BP John Ross | 25 Jan 2017 | Walk in freezer is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Made work area safe. Assessed and found that the controller was faulty. Removed and replaced with new. Tested and all was in good working condition., |  | 2 | 450 | 900 | 1380 | Controller, | 60 | 510 | 2790 | 390.6 | 3180.6
8067469 | B52 | BP Escombe | 04 Feb 2017 | Clover chiller is leaking badly | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Barricaded work area with metal fencing and erected mobile tower scaffold. Ran pipe work and fitted new drain pipe for the chiller. , |  | 4 | 450 | 1800 | 3178 | Scaffolding complete with safety signs, guard rails and toe boards, 50mm PVC pipe, PVC fittings and PVC weld, | 60 | 510 | 5488 | 768.32 | 6256.32
8067670 | B52 | BP Sibaya | 06 Feb 2017 | Shop aircon not working at all. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Replaced two evaporator probe sensors. Tested and all was in good working condition. , |  | 3 | 450 | 1350 | 1442 | Probe Sensors , | 60 | 510 | 3302 | 462.28 | 3764.28
8067991 | B52 | BP Kwa Mashu Service Station | 08 Feb 2017 | Freezer motto/fan is completely covered by ice | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Defrost the system and removed all ice from the coils. Cleaned coils. Called back to site by the dealer. Checked wiring and gas pressure. Pressure was holding and the cycle was working fine. Defrost timer working fine. Reinstated sensor to correct position. , |  | 8 | 450 | 3600 | 525 | Coil cleaner , | 0 | 0 | 4125 | 577.5 | 4702.5
8067985 | B52 | BP Kwa Mashu Service Station | 08 Feb 2017 | Freezer meter off - no power, no switch from DB looks tripped | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found that the wiring on the unit was burnt. Isolated and re-wired the unit. Tested and found all was in good working condition. , |  | 4 | 450 | 1800 | 490 | Wiring , | 44 | 374 | 2664 | 372.96 | 3036.96
8068142 | B52 | Montwood Motors | 09 Feb 2017 | Air con is down -not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found that the HP switch was faulty. Removed and replaced with new. Tested and found gas pressure holding. , |  | 2 | 563 | 1126 | 2295.4 | HP Switch , | 53 | 450.5 | 3871.9 | 542.07 | 4413.97
8068041 | B52 | Drive In Motors | 09 Feb 2017 | Display fruit and vegetables fridge not maintaining temp | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found that the unit is working fine. The controller must be changed in future due to it reading incorrect temperature. , |  | 0 | 563 | 0 | 800 | Call Out Charge as per agreed rate, | 0 | 0 | 800 | 112 | 912
8068042 | B52 | Reservoir Hills Service Statio | 09 Feb 2017 | Cold drink chiller is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Removed faulty solenoid valve to dispose and fitted new. Washed and cleaned condenser coils. , |  | 2 | 450 | 900 | 2904.89 | Solenoid Valve , Coil cleaner , | 32 | 272 | 4076.89 | 570.76 | 4647.65
8067047 | B52 | Moore Rd Service Station | 10 Feb 2017 | Door seals and handle need replacement | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Made work area safe. Removed all old rubber seals to dispose and fitted new. Fitted new door handle. Cleaned work area to complete. , |  | 4 | 563 | 2252 | 2479 | Door handle , Door rubbers and seals , | 52 | 442 | 5173 | 724.22 | 5897.22
8067048 | B52 | Moore Rd Service Station | 10 Feb 2017 | Freezer requires new door seals and handle | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Made work area safe. Found the cool drink fridge gas was low and seals were damaged. Removed all old rubber seals to dispose and fitted new. Fitted new door handle. Re-gassed unit. Cleaned work area to complete. , |  | 3 | 450 | 1350 | 3194 | Door handle , Door rubbers and seals , Gas 404A, | 0 | 0 | 4544 | 636.16 | 5180.16
8067184 | B52 | BP Bluff | 10 Feb 2017 | Ice mounting in the fridge | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Switched the unit off. Defrost ice and removed all ice to dispose. Cleaned work area. , |  | 4 | 450 | 1800 | 0 | , | 70 | 595 | 2395 | 335.3 | 2730.3
8067046 | B52 | Moore Rd Service Station | 10 Feb 2017 | Milk chiller is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Found that the gas was low. Re-gassed the unit and monitored the temperature. , |  | 2 | 450 | 900 | 1900 | Gas, | 0 | 0 | 2800 | 392 | 3192
8068853 | B52 | BP Sibaya | 16 Feb 2017 | Shop air con not working at all | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found water in the electrical isolator. Removed water and sealed the unit. , |  | 1 | 450 | 450 | 70 | Sealer , | 65 | 552.5 | 1072.5 | 150.15 | 1222.65
[8 empty] | 54 |  | 23703 | 83743.82 |  | 706 | 6001 | 113447.82 | 15882.69 | 129330.51