## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8068524 | B59 | BP Bullion Boulevard Express | 13 Feb 2017 | The temp for the dairy chiller is too high | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found the unit is working fine. Unit was on defrost cycle. Drip tray was against the compressor causing a noise. Re-positioned to eliminate noise. Monitored the temperature. , |  | 1 | 450 | 450 | 0 | , | 60 | 510 | 960 | 134.4 | 1094.4
8068655 | B59 | Drive In Motors | 14 Feb 2017 | Water leaking from refrigerator unit | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Repaired drip tray with sealer to seal off from leaking. Cleaned and water tested. , |  | 2 | 450 | 900 | 92 | Sealer, | 120 | 1020 | 2012 | 281.68 | 2293.68
8070282 | B59 | BP Chatsworth Circle | 25 Feb 2017 | walk in frezzer at 10 degrees for the last 3 HOURS | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Defrost evaporator coils. Re-wired fan to be off on defrost cycle. Drain heater is not working. Left freezer working fine. Ordered drain heater to replace. , |  | 3 | 450 | 1350 | 259 | Wiring, gloves, tape, dust mask, | 60 | 510 | 2119 | 296.66 | 2415.66
8070386 | B59 | BP Bullion Boulevard Express | 27 Feb 2017 | Dairy chiller is not working ... ... | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found the unit was off on the HP. Reset and traced fault to be a faulty condenser fan motor. Quoted to replace. Display fridge wiring was burnt. Isolated unit and re-wire the entire unit. Tested and all was working fine. , |  | 3 | 450 | 1350 | 1329 | Wiring, gloves, tape, dust mask, | 60 | 510 | 3189 | 446.46 | 3635.46
8070594 | B59 | BP Bluff | 28 Feb 2017 | Fridge temp is too high ... | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Found a gas leak on the system and a faulty solenoid valve. Repaired gas leak and replaced solenoid valve. Re-gassed the unit. Tested the system and found no problems. , |  | 3 | 563 | 1689 | 2680 | Gas, Solenoid Valve , | 60 | 510 | 4879 | 683.06 | 5562.06
8070850 | B59 | Umlazi Service Centre | 01 Mar 2017 | all drainage from dairy chiller and walk in chiller are blocked and is now flooding the shop. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Unblocked six drains and flushed with water. , |  | 2 | 450 | 900 | 300 | Drain cleaner , | 68 | 578 | 1778 | 248.92 | 2026.92
8071197 | B59 | New Germany Service Centre | 02 Mar 2017 | The walk in chiller is not working. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found that a electrician is required to attend to the faulty db board., |  | 0 | 563 | 0 | 800 | Call Out Charge as per agreed rate, | 0 | 0 | 800 | 112 | 912
8069908 | B59 | BP Bullion Boulevard Express | 03 Mar 2017 | Repairs to air con system ... | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found the aircon had no fillers. Fitted new filter to the aircon. , |  | 2 | 563 | 1126 | 529 | Filter , | 60 | 510 | 2165 | 303.1 | 2468.1
8070087 | B59 | BP Bluff | 03 Mar 2017 | Polony chillers temp too high | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Made work area safe. Poured water to the heating by pass to cool down. Re-gassed two systems and monitored. Temperature was dropping. , |  | 2 | 563 | 1126 | 2800 | Gas, | 60 | 510 | 4436 | 621.04 | 5057.04
8070046 | B59 | BP Sibaya | 03 Mar 2017 | Dairy chiller is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found that the chiller is working fine. Defrost cycle is working the way it should be and temperature settings are correct. , |  | 0 | 563 | 0 | 800 | Call Out Charge as per agreed rate, | 0 | 0 | 800 | 112 | 912
8068882 | B59 | BP Chatsworth Circle | 03 Mar 2017 | Under bar fridge compressor is faulty | Reactive Maintenance | Cordon of the work area complete with safety cones, danger tape and warning signs. Isolate power to the fridge and place a lock tag on the DB. Remove the defective compressor, capilree, pencil dryer and dryer. Dispose of all defective components safely. Install a new Embrako compressor, capilree, pencil dryer and dryer. Prepare and re-gas the fridge. Remove lock out tag from the DB and turn power on. Conduct a test to insure that the fridge is working correctly. Clean and make work area safe, |  | 7 | 450 | 3150 | 7169.68 | Gas 134a, Capilree, Embrako Compressor, Dryer, Pencil Dryer, | 60 | 577.2 | 10896.88 | 1525.56 | 12422.44
8069819 | B59 | BP Prospecton Road Service Sta | 03 Mar 2017 | Air curtain is not blowing | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Stripped unit and cleaned out ventilators. Cleaned and washed fans and covers. Reinstated and tested. , |  | 2 | 450 | 900 | 0 | , | 70 | 595 | 1495 | 209.3 | 1704.3
[8 empty] | 27 |  | 12941 | 16758.68 |  | 678 | 5830.2 | 35529.88 | 4974.18 | 40504.06