## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8071760 | B62 | BP Bluff | 06 Mar 2017 | Ice is mounting on the shelf | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Removed damaged heater element and replaced with new. Changed the drain pipe. Tested and all was working fine. , |  | 3 | 450 | 1350 | 3014 | Drain pipe, Heater Element , | 60 | 510 | 4874 | 682.36 | 5556.36
8072033 | B62 | BP Ridge Oasis | 08 Mar 2017 | Wild Bean kitchen and back Office air conditioners are leaking | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Unblocked the drain pipe. Returned to site with issuer to access roof top. Replaced faulty 30uf capacitor with new. Unit is in a bad condition and needs to be replaced. , |  | 2 | 450 | 900 | 350 | Capacitor, | 120 | 1020 | 2270 | 317.8 | 2587.8
8072037 | B62 | BP Bluff | 08 Mar 2017 | Fridge is leaking ... ... | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Found drain was blocked. Unblocked using water and drain cleaner. Tested and found no blockage. , |  | 3 | 450 | 1350 | 350 | Drain cleaner , | 60 | 510 | 2210 | 309.4 | 2519.4
8072102 | B62 | Araf Fuel Centre | 08 Mar 2017 | 2 Door storeroom chiller is making loud noise. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found that the chiller was working fine. Found that the belt was touching the condenser. Stripped the unit and re-adjusted the belt. Re-assemble and tested. No noises found. , |  | 2 | 450 | 900 | 0 | , | 70 | 595 | 1495 | 209.3 | 1704.3
8072104 | B62 | Araf Fuel Centre | 08 Mar 2017 | cold drink fridge not cooling to the required standard. there is an abnormal noise coming from the motor. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Tested and found that the condenser is making a noise. Opened covers and stripped the unit. Tighten loose bolts and nuts from the compressor to the fan. Reassemble unit and found all was working fine. , |  | 3 | 450 | 1350 | 0 | , | 0 | 0 | 1350 | 189 | 1539
8072197 | B62 | Araf Fuel Centre | 09 Mar 2017 | Milk dairy chiller not cooling -temp 20 degrees | Reactive Maintenance | Isolate the power to the chiller with a lock out and tag. Install a new Sercumcee compressor unit and drier. Prepare and re-gas the unit. Recommission unit and conduct a test to insure that the unit is correctly working. Clean and make work area safe., |  | 8 | 450 | 3600 | 20295.92 | Sercumcee Compressor, R404 Gas, Dryer, | 40 | 340 | 24235.92 | 3393.03 | 27628.95
8072363 | B62 | BP Escombe | 10 Mar 2017 | Dairy chiller is leaking excessively | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Drain pipes were moved out of position. Refitted and secured back into position. , |  | 1 | 450 | 450 | 0 | , | 52 | 442 | 892 | 124.88 | 1016.88
8072590 | B62 | BP Raisethorpe | 13 Mar 2017 | Island fridge is not cooling -temp at 19 degrees | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed work to be completed. Removed faulty thermostat, solenoid valve and expansion valve to safely dispose. Fitted new components. Topped up unit with R404 gas. Tested and found no faults. , |  | 9 | 450 | 4050 | 3500 | Thermostat , Solenoid Valve , Expansion valve, R404 Gas , | 60 | 510 | 8060 | 1128.4 | 9188.4
8069405 | B62 | BP Prospecton Road Service Sta | 13 Mar 2017 | Chiller 2 is not cooling | Reactive Maintenance | Isolate power using lock tag on the DB. Install a new 2.5Hp Compressor, 3/8 Dryer, controller unit, probes and control panel. Prepare and re-gas the unit. Recommission unit. Clean and make work area safe., |  | 8 | 450 | 3600 | 17547.4 | Probe, 2.5HP Compressor 220V, R404 Gas, Controller, Control Panels, 3/8 Dryer , | 61 | 518.5 | 21665.9 | 3033.23 | 24699.13
8072727 | B62 | BP Clare Road | 14 Mar 2017 | Walk in chiller temp not working Fridge is warm. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Repaired gas leak and re-gassed the unit. , |  | 2 | 563 | 1126 | 2250 | Gas, | 34 | 289 | 3665 | 513.1 | 4178.1
8072697 | B62 | Drive In Motors | 14 Mar 2017 | Freezer alarm and Error message | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found that the controller and sensors were faulty. Removed and replaced with new. Tested and found all was in good working condition. , |  | 3 | 450 | 1350 | 3397 | Controller, Sensors , | 70 | 595 | 5342 | 747.88 | 6089.88
8070867 | B62 | BP Verulam | 16 Mar 2017 | Drains blocked . . . . . . . .. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cordon off work area and found drain pipe is to small causing the drain to block. Unblocked the drain. Drain pipe must be replace to stop the drain from blocking in future. , |  | 2 | 563 | 1126 | 350 | Drain cleaner , | 32 | 272 | 1748 | 244.72 | 1992.72
8072817 | B62 | Moore Rd Service Station | 17 Mar 2017 | Fridge door handle is broken | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Attended to site and assessed. Commenced to supply to purchase the exact match. Returned to site, removed the broken handle and replaced with new. , |  | 2 | 563 | 1126 | 1889 | Handle , | 52 | 442 | 3457 | 483.98 | 3940.98
8072915 | B62 | BP Bluff | 17 Mar 2017 | Fridge is leaking . . . . . | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cordon off work area and assessed. Unblocked the main drain pipe. , |  | 1 | 450 | 450 | 175 | Drain cleaner , | 65 | 552.5 | 1177.5 | 164.85 | 1342.35
[8 empty] | 49 |  | 22728 | 53118.32 |  | 776 | 6596 | 82442.32 | 11541.93 | 93984.25