## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8077320 | B75 | La Lucia Ridge Oasis | 25 Apr 2017 | dairy chiller temp. to high +16 degrees | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Defrost unit and removed all ice build up. Adjusted fan blades., |  | 5 | 450 | 2250 | 0 | , | 34 | 289 | 2539 | 355.46 | 2894.46
8077749 | B75 | BP Raisethorpe | 25 Apr 2017 | Dairy chiller no 2 is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Replaced probes and reprogrammed the controller., |  | 1 | 750 | 750 | 718 | Probe, | 120 | 1020 | 2488 | 348.32 | 2836.32
8076039 | B75 | BP Church Street | 25 Apr 2017 | Air con in shop not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Conducted general commissioning to the unit. Clean out and assessed. Unit in working fine. , |  | 1 | 450 | 450 | 0 | , | 110 | 935 | 1385 | 193.9 | 1578.9
8077155 | B75 | BP Waterloo | 25 Apr 2017 | office aircon unit is not cooling. | Reactive Maintenance | Isolate the power to the air conditioner units and place lock out tag on the DB. Decommission the old unit which is in a very bad state and obsolete and safely dispose. Supply and install a new 12000 BTU Carrier unit and reconnect. Remove the lock out tag and conduct to insure that the unit is operating correctly. Clean up and make safe the work area., |  | 8 | 450 | 3600 | 13692.72 | Copper pipes, Armeflex, Carrier 12000BTU, Isolator 30AMP, R22 Gas, Consumables (Tread tape, cabling, lugs ), | 40 | 340 | 17632.72 | 2468.58 | 20101.3
8077120 | B75 | BP Sibaya | 25 Apr 2017 | Office air con is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found that the contractor was faulty on the compressor. Replaced with new. , |  | 3 | 563 | 1689 | 2335.9 | Contactor , | 70 | 595 | 4619.9 | 646.79 | 5266.69
8076791 | B75 | BP Verulam | 25 Apr 2017 | Air con in the bakery is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cleaned out coils and drip tray. , |  | 2 | 563 | 1126 | 350 | Coil cleaner , | 32 | 272 | 1748 | 244.72 | 1992.72
8075647 | B75 | Montwood Motors | 25 Apr 2017 | Office air con is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Repaired gas leak and re-gassed the unit. , |  | 2 | 563 | 1126 | 1950 | Gas R22, | 70 | 595 | 3671 | 513.94 | 4184.94
8073802 | B75 | Araf Fuel Centre | 25 Apr 2017 | Office air con is leaking | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cleaned drip tray and unblocked the drain pipe. Found no leaks. , |  | 2 | 563 | 1126 | 0 | , | 60 | 510 | 1636 | 229.04 | 1865.04
8076133 | B75 | BP Ridge Oasis | 25 Apr 2017 | Office air con is leaking water from drip tray | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Unblocked drain pipe and cleaned fan motor. , |  | 2 | 450 | 900 | 0 | , | 80 | 680 | 1580 | 221.2 | 1801.2
8077903 | B75 | BP Raisethorpe | 25 Apr 2017 | Island chiller is not working , temp at +15 | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Repaired the leak on the expansion valve and re-gassed the unit. , |  | 3 | 450 | 1350 | 1950 | Gas 404A, | 120 | 1020 | 4320 | 604.8 | 4924.8
[8 empty] | 29 |  | 14367 | 20996.62 |  | 736 | 6256 | 41619.62 | 5826.75 | 47446.37