## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8078475 | B81 | BP Verulam | 12 May 2017 | 1 x Air Conditioning unit in cashier area leaking water very badly and 1 x Air water very Conditioning unit in shop leaking badly | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Attended to site and was informed that all aircons will be replaced by BJ Cooling. Call out charges apply. , |  | 0 | 563 | 0 | 800 | Call Out Charge as per agreed rate, | 0 | 0 | 800 | 112 | 912
8079185 | B81 | BP Sibaya | 12 May 2017 | Shop air con is not working ... ... . | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Washed and cleaned condenser coils and filters. Adjusted gas pressure accordingly. , |  | 1 | 450 | 450 | 350 | Coil cleaner , | 60 | 510 | 1310 | 183.4 | 1493.4
8076013 | B81 | Reservoir Hills Service Statio | 12 May 2017 | Freezer is not working ... ... ... .. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Install a new electronic Danfoss controller, 2 probe sensors and 2 circuit breakers. Recommission unit and conduct a test to insure that the unit is correctly functioning. Clean and make work area safe. , |  | 5 | 450 | 2250 | 4774.3 | Probe Senser, Screen Cable, Circuit Breaker, Danfoss Electronic Controller, | 22 | 187 | 7211.3 | 1009.58 | 8220.88
8079355 | B81 | Reservoir Hills Service Statio | 12 May 2017 | Freezer room fan motor not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Defrost and removed all ice build up. Replaced defective evaporator fan motor with new. Adjusted program settings., |  | 4 | 450 | 1800 | 2659 | Evaporator fan motor and fittings , | 0 | 0 | 4459 | 624.26 | 5083.26
8079358 | B81 | BP Raisethorpe | 12 May 2017 | WBC stainless steel food bar fridge fan broken | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Removed damaged condenser fan motor to safely dispose and fitted new. , |  | 2 | 563 | 1126 | 1189 | Ziel Dia Fan Motor, | 62 | 527 | 2842 | 397.88 | 3239.88
8079632 | B81 | BP Raisethorpe | 12 May 2017 | Juice chiller not working -temp too high | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Repaired gas leak on the expansion valve and re-gassed the unit. , |  | 2 | 450 | 900 | 650 | Gas, | 130 | 1105 | 2655 | 371.7 | 3026.7
8079563 | B81 | BP Northdene | 12 May 2017 | Deep freezer shelves broken ... ... ... | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cordon off work area to make safe. Repaired and secured shelving. , |  | 2 | 450 | 900 | 0 | , | 65 | 552.5 | 1452.5 | 203.35 | 1655.85
8079442 | B81 | BP Raisethorpe | 12 May 2017 | Island food chiller not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cordon off work area and assessed. Unit was short of gas. Repaired gas leak on the coils and adjusted probe settings. Topped up unit with gas. , |  | 2 | 750 | 1500 | 1950 | Gas 404A, | 130 | 1105 | 4555 | 637.7 | 5192.7
8079755 | B81 | BP Arena Park | 12 May 2017 | Air con drain pipe is leaking | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found aircon drain pipe was damaged. Cut and removed damaged section. Replaced with new pipe and fittings. , |  | 2 | 450 | 900 | 419 | PVC pipe and fittings , | 60 | 510 | 1829 | 256.06 | 2085.06
8079571 | B81 | BP Cascades Service Station | 12 May 2017 | Walk in freezer not working . . . . . . | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Defrosted evaporator coils. Checked gas pressure and adjusted programme settings., |  | 2 | 563 | 1126 | 0 | , | 170 | 1445 | 2571 | 359.94 | 2930.94
8079646 | B81 | BP Escombe | 12 May 2017 | Plug point burnt . . . . . | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found that the wall socket was faulty. Electrician to attend. Call out charges apply. , |  | 0 | 563 | 0 | 800 | Call Out Charge as per agreed rate, | 0 | 0 | 800 | 112 | 912
8079855 | B81 | BP Kwa Mashu Service Station | 12 May 2017 | Compressor has iced up . . . . , | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Defrosted evaporator coil, replaced heater element and repaired burnt wiring., |  | 2 | 450 | 900 | 1298 | Purpose made Heater element, wiring and tape , | 40 | 340 | 2538 | 355.32 | 2893.32
[8 empty] | 24 |  | 11852 | 14889.3 |  | 739 | 6281.5 | 33022.8 | 4623.19 | 37645.99