## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8079583 | B84 | BP John Ross | 22 May 2017 | Chiller unit is not chilling ... | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cordon off work area and assessed. Removed ice build up. Fitted new copper drain with drain heater and check operation. , |  | 3 | 450 | 1350 | 2162.5 | Heater tape, Copper tubing and fittings, | 30 | 255 | 3767.5 | 527.45 | 4294.95
8081301 | B84 | BP Northdene | 24 May 2017 | Walk in freezer tripping on DB Board. Temp is +2 degrees | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Repaired burnt wiring on control, replaced fan motor. Topped up gas and tested. , |  | 3 | 450 | 1350 | 2040 | Fan motor, Gas 404A, | 60 | 510 | 3900 | 546 | 4446
8080989 | B84 | BP Sibaya | 24 May 2017 | Air con unit tripping on error | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found that the unit tripped. Condenser panel fallen off. Re-secured and reset power to clear the error. , |  | 2 | 563 | 1126 | 0 | , | 62 | 527 | 1653 | 231.42 | 1884.42
8081092 | B84 | BP Arena Park | 24 May 2017 | Shop air con is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Stripped the unit to assess. Found loose connection on the over loading. Secured the wiring and reassembled the unit. , |  | 2 | 563 | 1126 | 0 | , | 60 | 510 | 1636 | 229.04 | 1865.04
8080759 | B84 | Chess Service Station | 24 May 2017 | Dairy chiller is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Adjusted temperature and reset defrost timer. , |  | 1 | 450 | 450 | 0 | , | 52 | 442 | 892 | 124.88 | 1016.88
8080460 | B84 | BP Northdene | 24 May 2017 | Chiller lights is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Replaced ballast, light bulbs and starters. Tested and lights were working fine. , |  | 2 | 450 | 900 | 500 | Light bulbs , Ballast and starters, | 60 | 510 | 1910 | 267.4 | 2177.4
8080428 | B84 | New Germany Service Centre | 24 May 2017 | Under bar chiller is not working | Reactive Maintenance | Isolate the power to the freezer with a lock out and tag. Install a new compressor unit and drier. Prepare and re-gas. Recommission unit and conduct a test to ensure that the unit is correctly working. Clean and make work area safe., |  | 2 | 450 | 900 | 4578 | Vacuum breaker, 404 Gas, Liquid Line Drier, Compressor, | 42 | 357 | 5835 | 816.9 | 6651.9
8080310 | B84 | BP Bluff | 24 May 2017 | Dairy upright lights are not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Replaced the faulty light bulb with new., |  | 1 | 450 | 450 | 120 | 39 watt light bulb , | 60 | 510 | 1080 | 151.2 | 1231.2
8080278 | B84 | BP Northdene | 24 May 2017 | Cold room is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found that the unit tripped and breaker was faulty. Removed and fitted new triple pole circuit breaker. Tested and all was working fine., |  | 1 | 450 | 450 | 643 | Circuit breaker 32 amp, | 60 | 510 | 1603 | 224.42 | 1827.42
8080105 | B84 | Drive In Motors | 24 May 2017 | Back office air is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Cleaned out condenser and replaced capacitor. Topped up gas , |  | 2 | 563 | 1126 | 1300 | Gas R22, Capacitor , | 70 | 595 | 3021 | 422.94 | 3443.94
8080230 | B84 | BP John Ross | 25 May 2017 | Deep freezer is not working .. .. .. .. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Repaired wiring on solenoid. Replaced the faulty defrost controller. Removed all ice build up and re-gassed the unit. , |  | 2 | 450 | 900 | 2463 | Danfoss controller , Gas 404A, | 30 | 255 | 3618 | 506.52 | 4124.52
[8 empty] | 21 |  | 10128 | 13806.5 |  | 586 | 4981 | 28915.5 | 4048.17 | 32963.67