## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8082199 | B86 | Daniels Auto Centre | 30 May 2017 | Air con is not working ... ... . . . | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found that the unit tripped on the overload multiplug. Reset and checked operation. , |  | 1 | 450 | 450 | 0 | , | 170 | 1445 | 1895 | 265.3 | 2160.3
8080500 | B86 | BP Sibaya | 30 May 2017 | Defrost cycle too long -failed audit | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Adjusted defrost cycle to optimal settings. , |  | 2 | 450 | 900 | 0 | , | 60 | 510 | 1410 | 197.4 | 1607.4
8080043 | B86 | BP Chatsworth Circle | 30 May 2017 | Stand up freezer is not working | Reactive Maintenance | Create a safe barricaded work area. Isolate the power to the freezer with a lock out and tag. Install a new compressor unit and drier. Transport the unit to our workshop and re-gas. Return to site with the unit and recommission unit. Conduct a test to ensure that the unit is correctly working., |  | 8 | 450 | 3600 | 4250 | R290 Gas, Drier, Compressor, | 120 | 1020 | 8870 | 1241.8 | 10111.8
8081622 | B86 | BP Arena Park | 30 May 2017 | Air con is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Unit cut off on safety. Adjusted pitch on fan blades and checked gas levels. , |  | 2 | 450 | 900 | 0 | , | 62 | 527 | 1427 | 199.78 | 1626.78
8081698 | B86 | BP Bluff | 30 May 2017 | Ice build up in chiller | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Found drip tray was broken. Removed ice from the evaporator coil. Returned to site and replaced faulty heater drain. Defrost and removed excess ice from the blower coil. Repaired the drip tray. , |  | 3 | 450 | 1350 | 728 | Drain heater , | 120 | 1020 | 3098 | 433.72 | 3531.72
8080927 | B86 | Bullion Boulevard Express | 01 Jun 2017 | Dairy chiller is not working ... | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found that the compressor was not running. Pressure tested and all was fine. Reset thermostat and lowered temperature. Monitored operations. , |  | 2 | 450 | 900 | 0 | , | 30 | 255 | 1155 | 161.7 | 1316.7
8081364 | B86 | Bullion Boulevard Express | 01 Jun 2017 | The sandwich chiller is not working it is off something burnt last night | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Found burnt wiring and loose connection on the unit. Rewired and repaired loose connection. , |  | 3 | 450 | 1350 | 259 | Wiring, tape and gloves , | 30 | 255 | 1864 | 260.96 | 2124.96
[8 empty] | 21 |  | 9450 | 5237 |  | 592 | 5032 | 19719 | 2760.66 | 22479.66