## Simple
Sevest Ref. | Invoice No. | Site Name | Date Logged | Issue / Incident Description | Category | Solution: Reason For ADHOC Billing | #R | Labour Hrs. | Rate | Labour Ttl. | Material Ttl. | Material Description | Mileage (Km) | Mileage Ttl | Inv Excl. | TAX | Inclusive | Approved | Seavest Comments | BP Comments
8150246 | B213 | BP Northdene | 15 Nov 2018 | Shop air con is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and topped up gas. Returned to site and replaced temperature display., |  | 3 | 550 | 1650 | 3100 | R22 gas, Temperature Display, | 100 | 915 | 0 | 0 | 6514.75
8153422 | B213 | Motorhaven | 07 Dec 2018 | Light tubes in the dairy/juice chiller has fused | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed job and to return to site with materials. Returned to site and replaced 8 T8 tubes on upright chiller. Tested and all is in order., |  | 3 | 550 | 1650 | 760 | T8 Light tube, | 120 | 1098 | 0 | 0 | 4034.2
8157839 | B213 | BP Dube Village Mall | 15 Jan 2019 | mans toilets is leaking all over we cant able to use it at all | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents, |  | 0 | 550 | 0 | 0 | , | 0 | 0 | 0 | 0 | 0
8157775 | B213 | BP Ridge Oasis | 15 Jan 2019 | In the ladies toilets water is leaking on ceiling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed job and returned to site and repaired leaking pipe. Replaced damaged ceiling board., |  | 2 | 430 | 860 | 90 | ceiling boards, | 204 | 1866.6 | 2816.6 | 422.49 | 3239.09
8158055 | B213 | BP Escombe | 15 Jan 2019 | Metal strip at the front of the shop entrance is protruding | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assess job and drill and install hiltis to secure angle iron. To return to site to Weld angle iron to strip., |  | 3 | 550 | 1650 | 0 | , | 92 | 841.8 | 0 | 0 | 2451.57
8154661 | B213 | Westville Autohouse | 23 Jan 2019 | Replaced air con controller timer MTC: | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found aircon controller switch blown. Returned to site and installed new switch., |  | 3 | 483.75 | 1451.25 | 1300 | Timer switch Legrand, | 80 | 732 | 3483.25 | 522.4875 | 4005.74
8159688 | B213 | BP Prospecton Road Service Sta | 30 Jan 2019 | Dairy chiller 1 is not cooling. It has a lot of ice build up. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found unit iced up. Defrosted ice and unit working correctly., |  | 2 | 483.75 | 967.5 | 0 | , | 60 | 549 | 1516.5 | 227.475 | 1743.98
8161821 | B213 | Reservoir Hills Service Statio | 15 Feb 2019 | dry wall in the store room damaged and now has a hole in it,could cause rest of wall to collapse. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed job and returned to site and replaced damaged drywall partitioning. Painted new drywall and allowed to dry., |  | 1 | 430 | 430 | 1850 | Dry wall board, Rhinolite and paint, | 48 | 439.2 | 0 | 0 | 3127.08
8163029 | B213 | BP Scottsville | 22 Feb 2019 | Part of the canopy is loose between pump 4 and 5 | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assess and repair part of canopy that is loose., |  | 1 | 550 | 550 | 0 | , | 182 | 1665.3 | 0 | 0 | 2409.6
8162868 | B213 | BP Kwa Mashu Service Station | 22 Feb 2019 | building roof is leaking from the office to the shop | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed leak in office and kiosk roof. Returned to site and waterproofed 12 metres of flashing. Tested for leaks and found none., |  | 3 | 550 | 1650 | 1100 | water proofing kit, | 44 | 402.6 | 0 | 0 | 3211.49
8162480 | B213 | New Germany Service Centre | 06 Mar 2019 | The ceiling just above the dairy fridge is falling apart. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and replaced damaged ceiling tiles above dairy fridge., |  | 1 | 550 | 550 | 180 | ceiling boards, | 40 | 366 | 0 | 0 | 1122.4
8162542 | B213 | BP Northdene | 07 Mar 2019 | office roof leaking, computers are at risk of being damaged | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Conducted assessement of office roof leak. Returned to site and waterproofed 6 metres of flashing., |  | 3 | 550 | 1650 | 550 | water proofing kit, | 100 | 915 | 0 | 0 | 3168.25
PM4578415 | B213 | Belfast 1 Stop | 12 Mar 2019 | As per Mandla Jama# Seavest to: Assess and repair faulty ladies and gents bathroom before the start of the school holidays. Fritz Van Der Merwe 013 2530433 | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Repaired the cracks on the blue arch with pollyfilla. Applied plaster primer and two coats Engen blue to the blue arch. , Female restroom: Create a safe barricaded work area. Isolate the water supply to female restroom. Conduct a service on 6 defective senior flush masters. Replace 6 non-functional senior flush masters with new. Supply and install 1 new Cobra push button tap and 1 pillar tap. Install 2 new toilet seat sets., Prepare and retile where required. Grout on completion, |  | 30 | 450 | 13500 | 87319.88 | Cobra push button tap, Toilet seat sets, Cobra senior flush master kits , Johnson 200 x 200 Wall Tiles, Tile adhesive, Cobra pillar tap (Stella), Tile grout, Cobra concealed senior flush master, Cobra junior flush master kits, Cobra junior flush master, Floor tiles 300 x300, Cobra flush pipe for urinal, | 1840 | 14996 | 0 | 0 | 133188.26
8165448 | B213 | Reservoir Hills Service Statio | 12 Mar 2019 | ceiling near the wild bean café leaking with rain... | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and waterproofed 12 metres of roof sheets., |  | 2 | 550 | 1100 | 1100 | water proofing kit, | 24 | 219.6 | 0 | 0 | 2506.54
8165460 | B213 | Reservoir Hills Service Statio | 12 Mar 2019 | Roof leaks due to heavy rain causing damages to ceiling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and waterproofed area around air ducts., |  | 2 | 550 | 1100 | 550 | water proofing kit, | 24 | 219.6 | 0 | 0 | 1874.04
8164898 | B213 | BP Ridge Oasis | 12 Mar 2019 | Gents Ablutions- the 2" water supply feeding into the toilets is leaking. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and repaired water leak, |  | 2 | 550 | 1100 | 0 | , | 204 | 1866.6 | 0 | 0 | 3135.59
8165470 | B213 | BP Ridge Oasis | 13 Mar 2019 | water coming through ceiling in multiple places with the current rain we are having | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assess and waterproof female toilet roof that is leaking., |  | 3 | 550 | 1650 | 1100 | water proofing kit, | 102 | 933.3 | 0 | 0 | 3821.8
8165514 | B213 | New Germany Service Centre | 13 Mar 2019 | There is a heavy leak in the roof of inside dry store | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Conducted assessment on roof leak., |  | 1 | 550 | 550 | 0 | , | 40 | 366 | 0 | 0 | 915.4
8163704 | B213 | BP Kwa Mashu Service Station | 14 Mar 2019 | Auto door not sensing to close automatically | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and swopped malfunctioning sensor with sensor from operator that is not in use. Reset snd adjusted sensor., |  | 1 | 488 | 488 | 0 | , | 22 | 201.3 | 0 | 0 | 792.7
8167243 | B213 | BP Church Street | 28 Mar 2019 | the forecourt canopy has a big hole and water is leaking badly | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assess and repair forecourt canopy, |  | 4 | 550 | 2200 | 0 | , | 170 | 1555.5 | 0 | 0 | 3766.83
8168029 | B213 | Moore Rd Service Station | 29 Mar 2019 | Roof leak at cashier kiosk | Scheduled Maintenance | Conducted risk assessment & completed necessary safety documents. Assess and waterproof roof area that is leaking., |  | 2 | 550 | 1100 | 550 | water proofing kit, | 22 | 201.3 | 0 | 0 | 1853
8167310 | B213 | BP Bluff | 01 Apr 2019 | male toilet roof leaking next to the light bulbs | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assess and waterproof roof that is leaking., |  | 2 | 550 | 1100 | 550 | water proofing kit, | 42 | 384.3 | 0 | 0 | 2063.45
8167288 | B213 | Chess Service Station | 01 Apr 2019 | Ceiling is leaking again .. .. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and waterproofed roof that is leaking., |  | 2 | 550 | 1100 | 1100 | water proofing kit, | 22 | 201.3 | 0 | 0 | 2485.5
8167630 | B213 | Drive In Motors | 05 Apr 2019 | Water leak on roof of cold room | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assess and return to site with spares to do repair., |  | 6 | 550 | 3300 | 3320 | Armaflex , R404a gas, | 152 | 1390.8 | 0 | 0 | 9212.42
8168711 | B213 | BP Bluff | 08 Apr 2019 | all air pressure pumps leaking from pump 1to8. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents, |  | 0 | 550 | 0 | 0 | , | 0 | 0 | 0 | 0 | 0
8169083 | B213 | BP Bluff | 09 Apr 2019 | Roof is leaking again .. .. .. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assess and waterproof flashing in office area., |  | 2 | 550 | 1100 | 550 | water proofing kit, | 42 | 384.3 | 0 | 0 | 2063.45
8167311 | B213 | BP Bluff | 09 Apr 2019 | external manual door not closing | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and removed old hinges and door lock. Replaced old hinges and lock with new. Tested door and it is working correctly., |  | 2 | 550 | 1100 | 350 | Hinges and door lock, | 42 | 384.3 | 0 | 0 | 1833.45
8169298 | B213 | BP Northdene | 10 Apr 2019 | Mens toilet door handle broken | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed door and removed broken lock set and fitted temporary lock set. Returned to site with new lock set. Removed temporary lock set and installed new lock set. Tested door and it is working correctly., |  | 2 | 550 | 1100 | 1077 | Door lockset with handles, | 100 | 915 | 0 | 0 | 3279.8
8170256 | B213 | BP Ridge Oasis | 16 Apr 2019 | Pipe supplying water to hand basin is leaking | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assess and repair water pipe supplying water to the hand basin in the WBC., |  | 5 | 550 | 2750 | 3794.84 | 54mm 5.5m copper pipe, 54mm straight coupler, 50mm Ball cock Valve, Nasco Flux, Blowtorch, Gas catridge, 2mm Solder wire, | 204 | 1866.6 | 0 | 0 | 7811.44
8170892 | B213 | Reservoir Hills Service Statio | 23 Apr 2019 | Underground storm water drain is blocked | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Arrived on site and found dealer arranged another plumber to unblock., |  | 0 | 550 | 0 | 800 | Call out charges as agreed, | 0 | 0 | 0 | 0 | 920
8171389 | B213 | BP Waterloo | 24 Apr 2019 | water pipe burst on site. no water available | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assess and repair burst water pipe ., |  | 3 | 550 | 1650 | 0 | , | 40 | 366 | 0 | 0 | 1904.4
8170908 | B213 | BP Umbilo | 24 Apr 2019 | roof leaking in cashier kiosk - wetting POS and WBC | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and waterproofed roof and clean gutters., |  | 3 | 550 | 1650 | 550 | water proofing kit, | 28 | 256.2 | 0 | 0 | 2410.63
8171205 | B213 | BP Bluff | 03 May 2019 | Roof leaking in shop, WBC and kiosk staff toilet | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assess and waterproof 10 metres of flashing., |  | 2 | 550 | 1100 | 1100 | water proofing kit, | 42 | 384.3 | 0 | 0 | 2695.95
8172005 | B213 | BP Dube Village Mall | 03 May 2019 | all 4 air-gauges are not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and removed 4 thumb triggers that was damaged. Installed four new thumb triggers., |  | 2 | 550 | 1100 | 1520 | Thumb triggers, | 48 | 439.2 | 0 | 0 | 3242.08
8172388 | B213 | BP Ridge Oasis | 05 May 2019 | The Cash Office Toilet is backing due to a blockage | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assess and found repair done by dealer., |  | 1 | 550 | 550 | 0 | , | 102 | 933.3 | 0 | 0 | 1567.8
8172587 | B213 | BP Ridge Oasis | 06 May 2019 | 1st Toilet In The Ladies is leaking on the flush pipe | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and repaired flush pipe., |  | 2 | 550 | 1100 | 0 | , | 102 | 933.3 | 0 | 0 | 2062.3
8172804 | B213 | BP Church Street | 14 May 2019 | 2 air pressure gages are not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assess and repair air pressure gauge, |  | 2 | 550 | 1100 | 0 | , | 170 | 1555.5 | 0 | 0 | 2777.83
8173743 | B213 | Reservoir Hills Service Statio | 14 May 2019 | Cashier Kiosk Bullet proof door not locking | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and adjusted door closer., |  | 1 | 550 | 550 | 0 | , | 22 | 201.3 | 0 | 0 | 726
8173740 | B213 | La Lucia Ridge Oasis | 14 May 2019 | shop and store room T Pannel rusty | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assess and replace cross and main tees in shop area., |  | 12 | 550 | 6600 | 1580 | Cross and Main Tees, | 30 | 274.5 | 0 | 0 | 8066.68
8173697 | B213 | BP Northdene | 14 May 2019 | KIOSK ROOF LEAKING,CAUSING DAMAGE TO CABLES | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assess and waterproofed flashing., |  | 2 | 550 | 1100 | 550 | water proofing kit, | 50 | 457.5 | 0 | 0 | 2147.63
8174275 | B213 | BP Chatsworth Circle | 22 May 2019 | Auto door sensor is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assess and adjusted approach distance and sensistivity on internal and external sensors., |  | 1 | 550 | 550 | 0 | , | 66 | 603.9 | 0 | 0 | 1326.99
8150605 | B213 | BP Umbilo | 23 May 2019 | Mens and ladies public toilets are leaking | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and repaired toilet leaks. Installed 3 new pan seats and covers., |  | 3 | 550 | 1650 | 650 | Pan seat and cover, | 28 | 256.2 | 0 | 0 | 2525.63
8171418 | B213 | Chess Service Station | 24 May 2019 | canopy drain is blocked | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents.Assessed and cleaned canopy gutters., |  | 2 | 550 | 1100 | 0 | , | 22 | 201.3 | 0 | 0 | 1220.5
8171240 | B213 | Chess Service Station | 24 May 2019 | Shop roof is leaking back office is flooded | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and waterproofed flashing., |  | 2 | 550 | 1100 | 1100 | water proofing kit, | 22 | 201.3 | 0 | 0 | 2485.5
8175220 | B213 | BP Ridge Oasis | 27 May 2019 | The 2 inch water supply pipe feeding the 4x toilets has burst | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed male toilet pipe.that has burst., |  | 5 | 550 | 2750 | 0 | , | 102 | 933.3 | 0 | 0 | 3545.8
8171218 | B213 | BP Escombe | 27 May 2019 | shop roof is leaking in various places . | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and waterproofed flashing., |  | 2 | 550 | 1100 | 550 | water proofing kit, | 46 | 420.9 | 0 | 0 | 2105.54
8175482 | B213 | BP Ridge Oasis | 28 May 2019 | 1st and 3rd toilets in the ladies public toilets are leaking. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and did temporary repair. Returned to site and installed new flush master pan connectors, |  | 6 | 550 | 3300 | 320 | Pan sealer and putty, Flushmaster pan connectors, | 204 | 1866.6 | 0 | 0 | 5481.59
8166569 | B213 | New Germany Service Centre | 03 Jun 2019 | Male and female toilets are leaking | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and sealed leak on toilet, |  | 1 | 550 | 550 | 90 | Pan sealer, | 40 | 366 | 0 | 0 | 1018.9
8176708 | B213 | BP Prospecton Road Service Sta | 11 Jun 2019 | There is a leak on an underground water pipe behind the toilet | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and repaired underground leak, |  | 8 | 550 | 4400 | 420 | Pipe and pipe fittings , | 120 | 1098 | 0 | 0 | 5701.7
8170003 | B213 | BP Berea E L | 11 Jun 2019 | Tiles are broken in front of shop | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and replaced damaged tile on entrance of shop., |  | 2 | 550 | 1100 | 370 | Cement,Grout,tile, | 120 | 1098 | 0 | 0 | 2953.2
8175612 | B213 | Reservoir Hills Service Statio | 14 Jun 2019 | Walk in chiller lights not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assess and repair walk in chiller lights which is not working., |  | 2 | 550 | 1100 | 570 | Ballast, tubes, | 24 | 219.6 | 0 | 0 | 2173.04
8178510 | B213 | BP Ridge Oasis | 18 Jun 2019 | Main water pipe is leaking near to the stop cock | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents, |  | 0 | 550 | 0 | 0 | , | 0 | 0 | 0 | 0 | 0
8179046 | B213 | BP Berea E L | 21 Jun 2019 | Chiller unit temp too high | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found condensor tripped. Reset unit and topped up unit with gas., |  | 1 | 550 | 550 | 400 | R404 Gas, | 60 | 549 | 0 | 0 | 1723.85
8174234 | B213 | Araf Fuel Centre | 25 Jun 2019 | Check and repair side door muffin freezer broken shelving. | Reactive Maintenance | Assessed and repaired broken shelving.., |  | 2 | 550 | 1100 | 0 | , | 34 | 311.1 | 1411.1 | 211.665 | 1622.77
8178552 | B213 | BP Kwa Mashu Service Station | 25 Jun 2019 | Repair ice freezer which is not freezing. | Reactive Maintenance | Assessed and found evaporator coils leaking. Topped up unit with gas and tested unit.., |  | 2 | 550 | 1100 | 3200 | R404 Gas, | 18 | 164.7 | 0 | 0 | 5134.41
8179203 | B213 | Chess Service Station | 25 Jun 2019 | Air con not working. Check and repair. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found phase on isolator burnt. Repaired phase on power cable and tested., |  | 2 | 550 | 1100 | 0 | , | 22 | 201.3 | 0 | 0 | 1526.4
8178898 | B213 | Drive In Motors | 25 Jun 2019 | Main walk in freezer is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found drain iced up. Defrosted drain pipe and replaced drain heater., |  | 3 | 550 | 1650 | 585 | Drain Heater, Armaflex , | 78 | 713.7 | 0 | 0 | 2948.7
8178892 | B213 | Reservoir Hills Service Statio | 25 Jun 2019 | Freezer room is not cooling .. . .. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found controller faulty. Removed faulty controller and replaced with new. Rewired controller and tested unit., |  | 2 | 550 | 1100 | 2060 | 213 Controller, PTC Sensor, | 24 | 219.6 | 0 | 0 | 3379.6
8178510 | B213 | BP Ridge Oasis | 01 Jul 2019 | Check and pair leaking water pipe. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and excavated to find water leak. Repaired leak and found all in order. Another leak was discovered and temporary fix done. Repaired second leak and bacfilled and closed excavation area., |  | 20 | 430 | 8600 | 770 | Pipe and pipe fittings , Sand and concrete mix, | 510 | 4666.5 | 0 | 0 | 16141.98
8178382 | B213 | BP Cascades Service Station | 01 Jul 2019 | Repair automatic main sliding door. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and refitted hanger bracket onto door. Refit trolley bracket onto track profile and realigned panels. Fitted new return pulley., |  | 3 | 550 | 1650 | 2618.5 | Return pulley (Incl spindle and bearing), | 174 | 1592.1 | 0 | 0 | 6739.69
8180172 | B213 | BP Richmond Road | 01 Jul 2019 | Main water supply between the municipal water meter to the building is leaking substantially | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents, |  | 0 | 550 | 0 | 0 | , | 0 | 0 | 0 | 0 | 0
8180070 | B213 | Reservoir Hills Service Statio | 01 Jul 2019 | WBC drain pipe blocked. Please assess and repair | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents, |  | 0 | 550 | 0 | 0 | , | 0 | 0 | 0 | 0 | 0
8178794 | B213 | Araf Fuel Centre | 02 Jul 2019 | Check and repair a faulty thermostat | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assess and found thermostat faulty. Removed faulty thermostat and replaced with new., |  | 1 | 550 | 550 | 380 | Thermostat, | 37 | 338.55 | 0 | 0 | 1458.83
8173934 | B213 | Chess Service Station | 02 Jul 2019 | To install air hose brackets. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents, |  | 0 | 550 | 0 | 0 | , | 0 | 0 | 0 | 0 | 0
8179373 | B213 | BP Raisethorpe | 12 Jul 2019 | Dairy chiller temp too high | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and repaired dairy chiller not working., |  | 1 | 550 | 550 | 0 | , | 174 | 1592.1 | 0 | 0 | 2463.42
8179390 | B213 | BP Umbilo | 12 Jul 2019 | Freezer room door not closing | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and repaired freezer room door., |  | 2 | 550 | 1100 | 0 | , | 28 | 256.2 | 0 | 0 | 1559.63
8180313 | B213 | BP Raisethorpe | 12 Jul 2019 | Dairy chiller is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found heater element faulty. Replaced faulty element with new., |  | 1 | 550 | 550 | 1748.8 | Heater element, | 174 | 1592.1 | 0 | 0 | 4474.54
8180181 | B213 | Daniels Auto Centre | 12 Jul 2019 | Cold drinks chiller is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and repaired fridge not working., |  | 1 | 550 | 550 | 0 | , | 178 | 1628.7 | 0 | 0 | 2505.51
8180013 | B213 | BP Church Street | 12 Jul 2019 | Shop air con is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and repaired shop aircon., |  | 3 | 550 | 1650 | 0 | , | 170 | 1555.5 | 0 | 0 | 3686.33
8180125 | B213 | BP West Street | 12 Jul 2019 | Cold Drinks chiller is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found unit low on gas. Regassed unit and found accumulator faulty. Returned to site and replaced faulty accumulator with new. Topped up unit with gas., |  | 3 | 550 | 1650 | 1650 | Accumulator, R22 gas, | 40 | 366 | 0 | 0 | 3666
8180251 | B213 | New Germany Service Centre | 12 Jul 2019 | Freezer room is not freezing | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and repair freezer not working., |  | 1 | 550 | 550 | 0 | , | 40 | 366 | 0 | 0 | 1053.4
8181922 | B213 | BP Dube Village Mall | 12 Jul 2019 | Wild bean tap water is licking a lot of water | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Removed tap head and fitted new washer. Replaced Tap Head and tested., |  | 1 | 550 | 550 | 0 | , | 24 | 219.6 | 0 | 0 | 747.04
8176526 | B213 | BP Verulam | 15 Jul 2019 | Attend to cashier kiosk door | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and replaced 12 v battery and mounted power supply on cashier kiosk door. Adjusted door closer., |  | 2 | 550 | 1100 | 520 | 12 Volt battery , | 42 | 384.3 | 0 | 0 | 2304.95
8175247 | B213 | BP Raisethorpe | 15 Jul 2019 | Walk in chiller door is not closing | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and repaired walk in chiller door, |  | 2 | 550 | 1100 | 260 | Door seal, | 174 | 1592.1 | 0 | 0 | 3394.92
8178478 | B213 | BP Raisethorpe | 15 Jul 2019 | Dairy chiller is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and repaired dairy chiller., |  | 1 | 550 | 550 | 0 | , | 174 | 1592.1 | 0 | 0 | 2463.42
8180660 | B213 | Chess Service Station | 16 Jul 2019 | Dairy chiller is leaking .. .. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found drain blocked. Flushed drainline and cleaned out cabinet., |  | 1 | 550 | 550 | 0 | , | 22 | 201.3 | 0 | 0 | 864
8181252 | B213 | BP Berea E L | 16 Jul 2019 | Chiller is not cooling .. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found unit tripped . Reset unit and it is working correctly., |  | 1 | 550 | 550 | 0 | , | 60 | 549 | 0 | 0 | 1263.85
8180189 | B213 | BP Berea E L | 16 Jul 2019 | Chiller-top section hot and bottom section cold | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found leak on expansion valve. and LP/HP switch faulty. Replaced switch and topped up unit with gas., |  | 4 | 550 | 2200 | 3150 | LP/HP Switch, R404a gas, | 60 | 549 | 0 | 0 | 6783.85
8165517 | B213 | New Germany Service Centre | 18 Jul 2019 | refrigeration pipes are leaking .. .. ... .. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and repaired leaking aircon., |  | 1 | 550 | 550 | 0 | , | 40 | 366 | 0 | 0 | 1053.4
8165123 | B213 | La Lucia Ridge Oasis | 18 Jul 2019 | Walk in chiller is not cooling | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found unit short of gas. Topped up gas and cleaned out condensor., |  | 1 | 550 | 550 | 2000 | R22 gas, | 10 | 91.5 | 0 | 0 | 3037.73
8155321 | B213 | Westville Autohouse | 18 Jul 2019 | Freezer room is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and found condensor fan motor tripped on control circuit. Bypassed to get freezer to work., |  | 2 | 550 | 1100 | 0 | , | 38 | 347.7 | 0 | 0 | 1664.86
8180284 | B213 | Palm Service Centre | 19 Jul 2019 | walk in fridge is not working | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and repaired upright freezer., |  | 2 | 550 | 1100 | 1880 | Contactor, R404 Gas, | 60 | 549 | 0 | 0 | 4058.35
8179112 | B213 | BP King | 23 Jul 2019 | Dairy Chiller, freezing stock and temp too high | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and replaced two probes on chiller., |  | 3 | 550 | 1650 | 780 | Probe, | 60 | 549 | 0 | 0 | 3425.85
8161424 | B213 | BP King | 23 Jul 2019 | Cashier kiosk door is off the hinges | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and replaced damaged hinges on door., |  | 3 | 550 | 1650 | 240 | Hinges, | 60 | 549 | 0 | 0 | 2804.85
8183297 | B213 | BP Chatsworth Circle | 24 Jul 2019 | Front shop door is not closing | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and checked for obstacles in travel path. Reset operator., |  | 1 | 550 | 550 | 0 | , | 66 | 603.9 | 0 | 0 | 1326.99
8179714 | B213 | Araf Fuel Centre | 24 Jul 2019 | Office air con making a loud noise | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed noisy aircon. Found drain fan faulty., |  | 1 | 550 | 550 | 0 | , | 46 | 420.9 | 0 | 0 | 1116.54
8182965 | B213 | BP Church Street | 24 Jul 2019 | Cashier kiosk door not locking automatically. | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Removed damaged cabling and replaced with new., |  | 2 | 550 | 1100 | 240 | Cabling, | 170 | 1555.5 | 0 | 0 | 3329.83
8183427 | B213 | Araf Fuel Centre | 24 Jul 2019 | Cashier kiosk door is not closing | Reactive Maintenance | Conducted risk assessment & Completed necessary safety documents. Assessed and door closer., |  | 2 | 550 | 1100 | 0 | , | 46 | 420.9 | 0 | 0 | 1473.04
8170359 | B213 | Palm Service Centre | 26 Jul 2019 | Heating strips not working on any of the doors | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and repaired coldroom heaters., |  | 2 | 550 | 1100 | 0 | , | 60 | 549 | 0 | 0 | 1896.35
8183706 | B213 | BP Waterloo | 26 Jul 2019 | Cashier security door is not closing | Reactive Maintenance | Conducted risk assessment & completed necessary safety documents. Assessed and pop riveted door closure., |  | 1 | 550 | 550 | 0 | , | 40 | 366 | 0 | 0 | 915.4
[8 empty] | 238 |  | 124746.75 | 142944.02 |  | 8563 | 76511.45 | 9227.45 | 1384.1175 | 378701.79